## Ch.1 Wiring in PVC Conduit comp
Chapter E - 01
Electrical Wiring in PVC Conduit
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
Recessed PVC Conduit Wiring with Modular accessories
1.1 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, Aluminum round tiles, 1.2 mm thick Hot Dipped Galvanized Modular Box with earth terminal, 6 A Modular switch, Modular face plate with grid plate, 3 pin ceiling rose / Holder /3 way connector, screws, making connections, testing etc. as required.
1.1.1 | Short point (up to 3 mtr.) | P. point | 291 | 48
1.1.2 | Medium point (up to 6 mtr.) | P. point | 509 | 83
1.1.3 | Long point (up to 10 mtr.) | P. point | 699 | 114
1.2 | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, Aluminium round tiles, 2 Nos Hot Dipped Galvanized M.S Modular box of 1.2 mm thick with earth terminal,2 Nos 6 A two way Modular switch, 3 pin ceiling rose / holder / 3 way connector ,Modular face plate with grid plate, screws, making connections, testing etc. as required.
1.2.1 | Short point (up to 3 mtr.) | P. point | 578 | 95
1.2.2 | Medium point (up to 6 mtr.) | P. point | 1014 | 166
1.2.3 | Long point (up to 10 mtr.) | P. point | 1395 | 227
1.3 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988)accessories, Hot Dipped Galvanized Modular box of 1.2 mm thick with earth terminal, 6 A modular switch, 3/5 pin 6 A modular socket, Modular face plate with grid plate, screws, making connections, testing etc. as required.
1.3.1 | On board | P. point | 324 | 41
1.3.2 | Short point (up to 3 mtr.) | P. point | 467 | 76
1.3.3 | Medium point (up to 6 mtr.) | P. point | 685 | 112
1.3.4 | Long point (up to 10 mtr..) | P. point | 875 | 143
1.4 | S&F following sizes (dia.) of ISI marked MMS ( IS:9537 P - III ) PVC conduit along with ISI marked (IS:3419-1988) accessories as required in recess including making jhiri in the wall,clamps at suitable spacing, covering conduit and making good the same as required.
1.4.1 | 20 mm | Mtr. | 33 | 7
1.4.2 | 25 mm | Mtr. | 47 | 10
1.4.3 | 32 mm | Mtr. | 70 | 15
1.4.4 | 40 mm | Mtr. | 101 | 22
1.4.5 | 50 mm | Mtr. | 152 | 33
Recessed PVC Conduit Wiring with Non Modular accessories
1.5 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, Aluminium round tiles, 1.2 mm thick Hot dipped Galavanized MS box with earth terminal, 6 A switch, 3 pin ceiling rose/holder / 3 way connector , 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.5.1 | Short point (up to 3 mtr.) | P. point | 213 | 35
1.5.2 | Medium point (up to 6 mtr.) | P. point | 431 | 70
1.5.3 | Long point (up to 10 mtr.) | P. point | 621 | 101
1.6 | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, Aluminium round tiles, 2 Nos 1.2 mm thick Hot dipped Galavanized MS box with earth terminal, 2 Nos 6 A two way switch,3 pin ceiling rose / holder/ 3 way connector, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.6.1 | Short point (up to 3 mtr.) | P. point | 402 | 66
1.6.2 | Medium point (up to 6 mtr.) | P. point | 839 | 137
1.6.3 | Long point (up to 10 mtr..) | P. point | 1219 | 199
1.7 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) in recessed ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, 1.2 mm thick Hot dipped Galavanized MS box with earth terminal of required size, 6 A switch, 3/5 pin 6 A socket, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.7.1 | On board | P. point | 114 | 15
1.7.2 | Short point (up to 3 mtr.) | P. point | 248 | 41
1.7.3 | Medium point (up to 6 mtr.) | P. point | 466 | 76
1.7.4 | Long point (up to 10 mtr..) | P. point | 656 | 106.9988
1.8 | S&F of following sizes of polypropelene corrugated flexible conduit including gland on both side of flexible conduit as required.
1.8.1 | 16 mm OD | Mtr. | 10 | 2
1.8.2 | 20 mm OD | Mtr. | 13 | 3
1.8.3 | 25 mm OD | Mtr. | 18 | 4
1.8.4 | 32 mm OD | Mtr. | 30 | 7
1.8.5 | 40 mm OD | Mtr. | 37 | 8
Surface PVC Conduit Wiring with Modular accessories
1.9 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, round tiles, 1.2 mm thick Hot Dipped Galvanized Modular Box with earth terminal/Surface mounted UPVC molded modular box, 6 A Modular switch,Modular face plate with grid plate, 3 pin ceiling rose / Holder /3 way connector, screws, making connections, testing etc. as required.
1.9.1 | Short point (up to 3 mtr.) | P. point | 279 | 36
1.9.2 | Medium point (up to 6 mtr.) | P. point | 488 | 62
1.9.3 | Long point (up to 10 mtr.) | P. point | 671 | 86
1.10. | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, round tiles, 2 Nos Hot Dipped Galvanized M.S Modular box of 1.2 mm thick with earth terminal/Surface mounted UPVC molded modular box, 2 Nos 6 A two way Modular switch, 3 pin ceiling rose / holder / 3 way connector ,Modular face plate with grid plate, screws, making connections, testing etc. as required.
1.10.1 | Short point (up to 3 mtr.) | P. point | 554 | 77
1.10.2 | Medium point (up to 6 mtr.) | P. point | 973 | 130
1.10.3 | Long point (up to 10 mtr.) | P. point | 1104 | 147
1.11 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988)accessories, Hot Dipped Galvanized Modular box of 1.2 mm thick with earth terminal/Surface mounted UPVC molded modular box, 6 A modular switch, 3/5 pin 6 A modular socket, Modular face plate with grid plate, screws, making connections, testing etc. as required.
1.11.1 | On board | P. point | 310 | 28
1.11.2 | Short point (up to 3 mtr.) | P. point | 448 | 57
1.11.3 | Medium point (up to 6 mtr.) | P. point | 657 | 84
1.11.4 | Long point (up to 10 mtr..) | P. point | 840 | 107
1.12 | S&F following sizes (dia.) of ISI marked MMS ( IS:9537 P - III ) PVC conduit along with ISI marked (IS:3419-1988) accessories as required on surface including heavy duty saddles with base at spacing of 0.60 mtr. etc as required.
1.12.1 | 20 mm | Mtr. | 32 | 6
1.12.2 | 25 mm | Mtr. | 45 | 9
1.12.3 | 32 mm | Mtr. | 67 | 13
1.12.4 | 40 mm | Mtr. | 97 | 18
1.12.5 | 50 mm | Mtr. | 146 | 28
Surface PVC Conduit Wiring with Non Modular accessories
1.13 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, round tiles, 1.2 mm thick Hot dipped Galvanized MS box with earth terminal of required size , 6 A switch, 3 pin ceiling rose/holder / 3 way connector , 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.13.1 | Short point (up to 3 mtr.) | P. point | 204 | 26
1.13.2 | Medium point (up to 6 mtr.) | P. point | 414 | 53
1.13.3 | Long point (up to 10 mtr.) | P. point | 596 | 76
1.14 | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, round tiles, 2 Nos 1.2 mm thick Hot dipped Galvanized MS box with earth terminal of required size, 2 Nos 6 A two way switch,3 pin ceiling rose / holder/ 3 way connector, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.14.1 | Short point (up to 3 mtr.) | P. point | 386 | 49
1.14.2 | Medium point (up to 6 mtr.) | P. point | 804 | 103
1.14.3 | Long point (up to 10 mtr..) | P. point | 1169 | 149
1.15 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) on surface ISI marked MMS ( IS:9537 P - III ) PVC conduit & it's ISI marked (IS:3419-1988) accessories, 1.2 mm thick Hot dipped Galvanized MS box with earth terminal of required size, 6 A switch, 3/5 pin 6 A socket, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
1.15.1 | On board | P. point | 109 | 10
1.15.2 | Short point (up to 3 mtr.) | P. point | 238 | 30
1.15.3 | Medium point (up to 6 mtr.) | P. point | 447 | 57
1.15.4 | Long point (up to 10 mtr..) | P. point | 630 | 80
Note:
1 | For specifications of Copper Conductor, Phenolic Laminated sheets and Electrical/Wiring accessories refer Chapter E - 04, E - 05 and E - 07.
2 | To ensure smooth Installation and workmanship, PVC conduit and it's accessories should be of same make.
3 | To maintain quality standards, Black conduits (which may be made from recycled material) are not to be used.
4 | To ensure strong bond, apply adhesive to the conduit surface before fixing Conduit accessories.
5 | Recessed conduit Jhiris will be made good condition after applying Wire chicken mesh
6 | In case of Twin control point Nearest switch board distance will be considered for Measurement
7

## Ch.2 wiring in Steel Conduit
Chapter E - 02
Electrical Wiring in Steel Conduit
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
Recessed Steel Conduit Wiring with Modular accessories
2.1 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed/surface ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) accessories, Aluminum round tiles,Hot Dipped Galvanized Modular Box 1.2 mm thick with earth terminal, 6 A Modular switch,3 pin ceiling rose / holder / 3 way connector ,Modular face plate with grid plate, pvc bushes, check nuts, screws, making connections, testing etc. as required.
2.1.1 | Short point (up to 3 mtr.) | P. point | 384 | 63
2.1.2 | Medium point (up to 6 mtr.) | P. point | 773 | 126
2.1.3 | Long point (up to 10 mtr..) | P. point | 1114 | 182
2.2 | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed/surface ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) accessories, Aluminum round tiles, 2 Nos Hot Dipped Galvanized Modular box 1.2 mm thick with earth terminal, 2 Nos 6 A two way Modular switch, 3 pin ceiling rose / holder / 3 way connector ,Modular face plate with grid plate, screws, pvc bushes, check nuts, making connections, testing etc. as required.
2.2.1 | Short point (up to 3 mtr.) | P. point | 763 | 125
2.2.2 | Medium point (up to 6 mtr.) | P. point | 1490 | 243
2.2.3 | Long point (up to 10 mtr..) | P. point | 2225 | 363
2.3 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) in recessed/surface ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) accessories, Hot Dipped Galvanized Modular box 1.2 mm thick with earth terminal, 6 A modular switch, 3/5 pin 6 A modular socket, Modular face plate with grid plate, pvc bushes, check nuts, screws, making connections, testing etc. as required.
2.3.1 | On board | P. point | 324 | 41
2.3.2 | Short point (up to 3 mtr.) | P. point | 560 | 92
2.3.3 | Medium point (up to 6 mtr.) | P. point | 948 | 155
2.3.4 | Long point (up to 10 mtr.) | P. point | 1290 | 211
2.4 | S&F following sizes (dia.) of ISI marked ( IS:9537 P - II ) rigid steel conduit with wall thickness according to IS Specified along with ISI marked (IS:14768 P-II 2003) accessories in recessed/surface using saddles, clamps, fasteners, pvc bushes, check nuts, as required including cutting jhiris in the wall and making good the same as required.
2.4.1 | 20 mm | Mtr. | 110 | 21
2.4.2 | 25 mm | Mtr. | 140 | 27
2.4.3 | 32 mm | Mtr. | 196 | 37
2.4.4 | 40 mm | Mtr. | 329 | 62
2.4.5 | 50 mm | Mtr. | 430 | 82
Recessed Steel Conduit Wiring with Non Modular accessories
2.5 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) marked accessories, Aluminum round tiles, 1.2 mm thick Hot dipped Galvanized MS box with earth terminal, 6 A switch, 3 pin ceiling rose/holder / 3 pin connector, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, pvc bushes, check nuts, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
2.5.1 | Short point (up to 3 mtr.) | P. point | 306 | 50
2.5.2 | Medium point (up to 6 mtr.) | P. point | 695 | 113
2.5.3 | Long point (up to 10 mtr.) | P. point | 1036 | 169
2.6 | Wiring of twin control point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) in recessed/surface ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) accessories, Aluminum round tles, 2 Nos 1.2 mm thick Hot dipped Galvanized MS box with earth terminal, 2 Nos 6 A two way switch, 3 pin ceiling rose / holder / 3 way connector, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, pvc bushes, check nuts, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
2.6.1 | Short point (up to 3 mtr.) | P. point | 587 | 95.9985
2.6.2 | Medium point (up to 6 mtr.) | P. point | 1365 | 223
2.6.3 | Long point (up to 10 mtr..) | P. point | 2049 | 334
2.7 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) in recessed/surface ISI marked ( IS:9537 P - II ) rigid steel conduit & it's ISI marked (IS:14768 P-II 2003) accessories, required size 1.2 mm thick , Hot dipped Galvanized MS box with earth terminal, 6 A switch, 3/5 pin 6 A socket, 3.0 mm thick ISI marked (IS:2036-1995) phenolic laminated sheet, pvc bushes, check nuts, Al.alloy / Cadmium plated iron/ brass screws, cup washers, making connections, testing etc. as required.
2.7.1 | On board | P. point | 114 | 15
2.7.2 | Short point (up to 3 mtr.) | P. point | 341 | 56
2.7.3 | Medium point (up to 6 mtr.) | P. point | 729 | 119
2.7.4 | Long point (up to 10 mtr..) | P. point | 1071 | 175
2.8 | S&F of following sizes of Galvanized steel corrugated flexible conduit with PVC coating including steel wire reinforced uPVC gland on both side of flexible conduit as required.
2.8.1 | 16 mm OD | Mtr. | 62 | 14
2.8.2 | 20 mm OD | Mtr. | 81 | 18
2.8.3 | 25 mm OD | Mtr. | 121 | 27
2.8.4 | 32 mm OD | Mtr. | 147 | 32
2.8.5 | 40 mm OD | Mtr. | 168 | 37
Note:
1 | For specifications of Copper Conductor, Phenolic Laminated sheets and Electrical/Wiring accessories refer Chapter E - 04, E - 05 and E - 07.
2 | All conduit accessories shall be of threaded type, and under no circumstances pin grip type or clamp grip type accessories shall be used.

## Ch 3 Wiring in uPVC trunking
Chapter E - 03
Electrical wiring in uPVC Trunking
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
Surface Wiring in uPVC Trunking with Modular accessories
3.1 | Wiring of light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) on surface ISI marked ( IS:14927 P - II ) uPVC trunking & it's accessories, Hot Dipped Galvanized Modular box 1.2 mm thick with earth terminal/ Surface mounted UPVC molded modular box, 6 A Modular switch, Modular face plate with grid plate, 3 pin ceiling rose/holder /3 way Connector, screws, making connections, testing etc. as required.
3.1.1 | Short point (up to 3 mtr.) | P. point | 288 | 47
3.1.2 | Medium point (up to 6 mtr.) | P. point | 502 | 82
3.1.3 | Long point (up to 10 mtr.) | P. point | 687 | 112
3.2 | Wiring of twin control light point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade (IS:694) of approved make on surface ISI marked ( IS:14927 P - II ) uPVC trunking & it's accessories, 2 No. Hot Dipped Galvanized Modular box 1.2 mm thick with earth terminal/ 2 No. Surface mounted UPVC molded modular box, 2 Nos 6 A two way Modular switch, 3 pin ceiling rose / holder/3 way Connector , Modular face plate with grid plate, screws, making connections, testing etc. as required
3.2.1 | Short point (up to 3 mtr.) | P. point | 573 | 94
3.2.2 | Medium point (up to 6 mtr.) | P. point | 999 | 163
3.2.3 | Long point (up to 10 mtr..) | P. point | 1371 | 224
3.3 | Wiring of 3/5 pin 6 amp. Light plug point with 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper conductor 1.1 kV grade and 1.5 sq. mm nominal size FR PVC insulated unsheathed flexible class 2 copper earth conductor 1.1 kV grade(IS:694) on surface ISI marked ( IS:14927 P - II ) uPVC trunking & it's accessories, Hot Dipped Galvanized Modular box 1.2 mm thick with earth terminal/Surface mounted UPVC molded modular box, modular 6 A switch, 3/5 pin 6 A modular socket, Modular face plate with grid plate, screws, making connections, testing etc. as required
3.3.1 | On board | P. point | 324 | 41
3.3.2 | Short point (up to 3 mtr.) | P. point | 464 | 76
3.3.3 | Medium point (up to 6 mtr.) | P. point | 678 | 111
3.3.4 | Long point (up to 10 mtr..) | P. point | 863 | 141
3.4 | S&F following sizes of ISI marked ( IS:14927 P - II ) uPVC trunking along with accessories like coupler, inner, outer, elbow, square box, tee, end cap etc. on surface with screws, expansion fasteners etc. as required.
3.4.1 | 20 mm x 12 mm | Mtr. | 30 | 7
3.4.2 | 25 mm x 12 mm | Mtr. | 36 | 8
3.4.3 | 32 mm x 12 mm | Mtr. | 45 | 10
3.4.4 | 25 mm x 16 mm | Mtr. | 44 | 10
3.4.5 | 38 mm x 16 mm | Mtr. | 71 | 16
3.4.6 | 38 mm x 25 mm | Mtr. | 80 | 18
3.4.7 | 38 mm x 38 mm | Mtr. | 106 | 23
3.4.8 | 50 mm x 16 mm | Mtr. | 123 | 27
3.4.9 | 50 mm x 50 mm | Mtr. | 207 | 46
3.4.10 | 75 mm x 50 mm | Mtr. | 501 | 111
3.4.11 | 75 mm x 75 mm | Mtr. | 655 | 145
3.4.12 | 100 mm x 50 mm | Mtr. | 816 | 180
3.4.13 | 100 mm x 100 mm | Mtr. | 1046 | 231
3.4.14 | 150 mm x 50 mm | Mtr. | 1242 | 274
3.4.15 | 150 mm x 100 mm | Mtr. | 1511 | 333
Note :
1 | For specifications of Copper Conductor, Phenolic Laminated sheets and Electrical/Wiring accessories refer Chapter E - 04, E - 05 and E - 07.
2 | PVC trunking shall be of good quality PVC, free from defects like deformation, unevenness, blisters, cavities etc.
3 | The thickness of the mini trunking and adaptable trunking shall be minimum 1 mm.
4 | To ensure smooth Installation and workmanship, PVC trunking and it's accessories should be of same make.

## Ch 4 Drawing of Wires & Submain
Chapter E - 04
Drawing of Wires and Submains
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
4.1 | Supplying and laying FR PVC insulated & unsheathed flexible copper conductor of following nominal sizes with ISI marked (IS:694) and as per IS 8130 : 2013 of 1.1 kV grade . Wire should be made from copper, stranding in acc. to IS:8130/IEC 60228 for lower watt loss , oxygen free for less chances of oxidization, insulation PVC type A/C/D , flame retardant as per IS 10810-53, better amperage rating as per IS:3961 part 5, in existing surface or recessed PVC/ MS conduit/casing capping making connections with Copper Lugs of suitable size, Ferrules,testing etc. as required.
4.1.1 | 1 x 1.5 sq.mm | Mtr. | 22 | 1.5
4.1.2 | 2 x 1.5 sq.mm | Mtr. | 43 | 3
4.1.3 | 3x 1.5 sq.mm | Mtr. | 64 | 4
4.1.4 | 4 x 1.5 sq.mm | Mtr. | 85 | 6
4.1.5 | 1 x 2.5 sq.mm | Mtr. | 35 | 3
4.1.6 | 2 x 2.5 sq.mm | Mtr. | 69 | 5
4.1.7 | 2 x 2.5 sq. mm. + 1x1.5sqmm | Mtr. | 90 | 7
4.1.8 | 3 x 2.5 sq.mm | Mtr. | 103 | 8
4.1.9 | 4 x 2.5 sq.mm | Mtr. | 138 | 10
4.1.10 | 1 x 4.0 sq.mm | Mtr. | 54 | 3
4.1.11 | 2 x 4.0 sq.mm | Mtr. | 107 | 6
4.1.12 | 3 x 4 sq. mm. | Mtr. | 161 | 9
4.1.13 | 4 x 4.0 sq.mm | Mtr. | 214 | 12
4.1.14 | 2 x 4.0 sq. mm. + 1 x 2.5 sq. mm. | Mtr. | 142 | 9
4.1.15 | 1 x 6.0 sq.mm | Mtr. | 75 | 4
4.1.16 | 2 x 6.0 sq.mm | Mtr. | 149 | 8
4.1.17 | 3 x 6.0 sq. mm. | Mtr. | 223 | 12
4.1.18 | 4 x 6.0 sq.mm | Mtr. | 298 | 16
4.1.19 | 2 x 6.0 sq. mm. + 1 x 2.5 sq. mm. | Mtr. | 184 | 12
4.1.20 | 2 x 6.0 sq. mm. + 1 x 4.0 sq. mm. | Mtr. | 205 | 13
4.1.21 | 1 x 10.0 sq.mm | Mtr. | 127 | 6
4.1.22 | 2 x 10.0 sq.mm | Mtr. | 505 | 11
4.1.23 | 4 x 10.0 sq.mm | Mtr. | 505 | 19
4.1.24 | 1 x 16.0 sq.mm | Mtr. | 199 | 8
4.1.25 | 2 x 16.0 sq.mm | Mtr. | 398 | 15
4.1.26 | 4 x 16.0 sq.mm | Mtr. | 796 | 30
4.2 | Supplying and Laying coaxial cable 75 ohm impedance with foam PE insulated solid bare copper inner conductor, and Ist outer conductor of bonded alum. tape and second outer conductor of alum. alloy braid in existing surface or recessed conduit/casing capping including making connections as required.
4.2.1 | RG - 6 | Mtr. | 24 | 3
4.2.2 | RG -11 | Mtr. | 55 | 7
4.3 | Supplying and Laying PE Insulated & PVC Sheathed unarmoured telephone cable with 0.5 mm dia. Solid Annealed electrolytic grade bare Copper Conductor as per IS: 8130/84 & confirming to TEC specification GR / WIR/06-03 March 2002 in existing surface or recessed conduit/casing capping. including ferruling on each pair for Identification etc. as required.
4.3.1 | 2 pair | Mtr. | 15 | 2
4.3.2 | 4 pair | Mtr. | 30 | 4
4.3.3 | 5 pair | Mtr. | 37 | 5
4.3.4 | 10 pair | Mtr. | 72 | 9
4.3.5 | 20 pair | Mtr. | 128 | 16
4.3.6 | 50 pair | Mtr. | 347 | 44
4.3.7 | 100 pair | Mtr. | 730 | 94
4.3.8 | 200 pair | Mtr. | 1401 | 180
4.4 | Supply and Laying of PE Insulated, PVC Inner Sheathed, armoured & PVC Sheathed Telephone Cable. with 0.5 mm thick Solid Annealed Bare Copper Conductor as per IS: 8130/84 telephone cable confirming to TEC specifications GR/WIR 06/03, Mar.-2002 in existing pipe / open trench / Cable tray / on surface including making necessary connection, testing etc. as required of size.
4.4.1 | 5 pair | Mtr. | 79 | 10
4.4.2 | 10 pair | Mtr. | 121 | 15
4.4.3 | 20 pair | Mtr. | 198 | 25
4.4.4 | 50 pair | Mtr. | 423 | 54
4.4.5 | 100 pair | Mtr. | 789 | 101
4.4.6 | 200 pair | Mtr. | 1527 | 196
4.5 | Supply and Laying of PE Insulated jelly filled Armoured Telephone Cable. with 0.6 mm thick Solid Annealed Bare Copper Conductor and confirming to TEC specifications confirming. to DOT GR/CUG-01/Aug.2003 in existing pipe / open trench / Cable tray / on surface including making necessary connection, testing etc. as required of size.
4.5.1 | 5 pair | Mtr. | 100 | 13
4.5.2 | 10 pair | Mtr. | 146 | 19
4.5.3 | 20 pair | Mtr. | 220 | 28
4.5.4 | 50 pair | Mtr. | 460 | 59
4.5.5 | 100 pair | Mtr. | 832 | 107
4.5.6 | 200 pair | Mtr. | 1561 | 200
4.6 | Supply & laying service connection with ISI marked (IS:694) 1100 Volts grade PVC insulated flat twin core sheathed solid aluminium conductor with 10 SWG G.I. Support wire duly clipped etc. as required.
4.6.1 | 2.5sq.mm | Mtr. | 44 | 6
4.6.2 | 4.0 sq.mm | Mtr. | 51 | 7
4.6.3 | 6.0 sq.mm | Mtr. | 61 | 8
4.6.4 | 10.0 sq.mm | Mtr. | 84 | 11
4.7 | Supply and Laying ISI marked P.V.C. insulated submersible cable confirming to(IS:694) and as per IS 8130 : 2013 of 1.1 kV grade . Wire should be made from copper, stranding in acc. to IS:8130/IEC 60228 for lower watt loss , oxygen free for less chances of oxidization, insulation PVC type A/C/D , flame retardant as per IS 10810-53, better amperage rating as per IS:3961 part 5, existing pipe / open trench / Cable tray / on surface including making connection etc. as required.
4.7.1 | 1.5 Sq.mm 3 core flat / Round | Mtr. | 79 | 10
4.7.2 | 2.5 Sq.mm 3 core flat / Round | Mtr. | 133 | 17
4.7.3 | 4.0 Sq.mm 3 core flat / Round | Mtr. | 196 | 25
4.7.4 | 6.0 Sq.mm 3 core flat / Round | Mtr. | 285 | 37
4.7.5 | 10.0 Sq.mm 3 core flat / Round | Mtr. | 480 | 61
4.7.6 | 16.0 Sq.mm 3 core flat / Round | Mtr. | 758 | 97
4.8 | Supply and laying following size twin parallel type Speaker cables made with multi wire, bright annealed flexible bare electrolytic grade copper conductor, insulated with specially formulated transparent grade PVC compound, red strip for identification in existing conduit etc. as required.
4.8.1 | 0.75 sq.mm | Mtr. | 27 | 3
4.8.2 | 1.0 Sq. mm | Mtr. | 33 | 4
4.8.3 | 1.5 Sq.mm | Mtr. | 51 | 7
4.8.4 | 2.5 Sq.mm | Mtr. | 71 | 9
4.9 | Supply and laying speaker cable of following size 2 core twin twisted multi stranded electrolytic grade copper conductor, overall PVC insulated and armoured cable (Blue colour) on surface/ above false ceiling including cost of GI spacers, saddles etc. as required.
4.9.1 | 0.75 sq.mm | Mtr. | 88 | 11
4.9.2 | 1.0 Sq. mm | Mtr. | 97 | 12
4.9.3 | 1.5 Sq.mm | Mtr. | 117 | 15
4.9.4 | 2.5 Sq.mm | Mtr. | 161 | 21
4.10 | Supply and laying PVC Insulated and PVC Round Sheathed Multi Core copper conductor (IS:694) and as per IS 8130 : 2013 of 1.1 kV grade . Wire should be made from copper, stranding in acc. to IS:8130/IEC 60228 for lower watt loss , oxygen free for less chances of oxidization, insulation PVC type A/C/D , flame retardant as per IS 10810-53, better amperage rating as per IS:3961 part 5, in existing pipe / open trench / Cable tray / on surface including making connection etc. as required.
4.10.1 | 1.5 sq.mm x 3 core | Mtr. | 81 | 10
4.10.2 | 1.5 sq.mm x 4 core | Mtr. | 106 | 13
4.10.3 | 1.5 sq.mm x 6 core | Mtr. | 167 | 13
4.10.4 | 1.5 sq.mm x 8 core | Mtr. | 225 | 29
4.10.5 | 2.5 sq.mm x 3 core | Mtr. | 131 | 17
4.10.6 | 2.5 sq.mm x 4 core | Mtr. | 171 | 22
4.10.7 | 2.5 sq.mm x 6 core | Mtr. | 273 | 35
4.10.8 | 2.5 sq.mm x 8 core | Mtr. | 362 | 46
4.10.9 | 4.0 sq.mm x 3 core | Mtr. | 210 | 27
4.10.10 | 4.0 sq.mm x 4 core | Mtr. | 276 | 35
4.10.11 | 4.0 sq.mm x 6 core | Mtr. | 425 | 54
Note:
1 | For item no. 4.1, 4.7 and 4.10 :
OEM must ensure that the PVC Copper Conductors is tested for compliance, through their in house laboratory accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and testing procedure as per IS:694.
2 | Upto 2.5 sqmm PVC Copper Conductor (IS:694), Class 2 wire should be used.
3 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 5 MS boxes
Chapter E - 05
Wiring Boxes & accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
5.1 | P & F 1.2 mm thick Hot dipped galvanized boxes with brass earthing terminal of following sizes (nominal size) in recessed/surface as required.
5.1.1 | 75mm x 75mm x 60mm | Each | 38 | 6
5.1.2 | 100mm x 100mm x 60mm | Each | 49 | 8
5.1.3 | 150mm x 75mm x 60mm | Each | 56 | 9
5.1.4 | 175mm x 100mm x 60mm | Each | 77 | 13
5.1.5 | 150mm x 150mm x 60mm | Each | 92 | 15
5.1.6 | 225mm x 100mm x 60mm | Each | 94 | 15
5.1.7 | 200mm x 150mm x 60mm | Each | 115 | 19
5.1.8 | 200mm x 125mm x 75mm | Each | 111 | 18
5.1.9 | 200mm x 250mm x 75mm | Each | 189 | 31
5.1.10 | 200mm x 250mm x 100mm | Each | 215 | 35
5.1.11 | 250mm x 300mm x 75mm | Each | 263 | 43
5.1.12 | 250mm x 300mm x 100mm | Each | 294 | 48
5.1.13 | 300mm x 375mm x 75mm | Each | 370 | 61
5.1.14 | 300mm x 375mm x 100mm | Each | 408 | 67
5.1.15 | 250mm x 100mm x 60mm | Each | 104 | 17
5.1.16 | 300mm x 100mm x 60mm | Each | 122 | 20
5.1.17 | 300mm x 300mm x 75mm | Each | 307 | 50
5.2 | P & F in position frame made out of M.S. angle (riveted or welded) finished with two coats of red oxide and two coats enamel paint including cutting, welding, holes etc.of following sizes as required.
5.2.1 | 25mm x 25mm x 3mm | Mtr. | 114 | 19
5.2.2 | 25mm x 25mm x 5mm | Mtr. | 187 | 31
5.2.3 | 35mm x 35mm x 5mm | Mtr. | 270 | 44
5.2.4 | 40mm x 40mm x 5mm | Mtr. | 311 | 51
5.2.5 | 50mm x 50mm x 6mm | Mtr. | 467 | 76
5.3 | P & Fixing Powder coated CRCA sheet enclosures on existing Structure by means of nuts and bolts and making holes , Din rail etc. as required.
5.3.1 | 1.2 mm thick | Sqm. | 1237 | 203
5.3.2 | 1.6 mm thick | Sqm. | 1650 | 270
5.3.3 | 2.0 mm thick | Sqm. | 2062 | 338
5.3.4 | 2.5 mm thick | Sqm. | 2578 | 423
5.4 | P & Fixing M.S. flat on existing angle iron frame and making required nos. of holes for fixing accessories including one coat of red oxide paint and two coats of enamel paint etc. as required.
5.4.1 | 25 mm x 3 mm | Mtr. | 62 | 10
5.4.2 | 25 mm x 5 mm | Mtr. | 102 | 17
5.4.3 | 32 mm x 5 mm | Mtr. | 135 | 22
5.4.4 | 40 mm x 6 mm | Mtr. | 195 | 32
5.4.5 | 50 mm x 6 mm | Mtr. | 245 | 40
5.5 | P & F paper phenolic resin bonded laminates confirming to IS : 2036 - 1995 for boxes/ frames including making holes for switches etc, with brass screws, washers/ zinc plated nut and bolts as required.
5.5.1 | 3.0 mm thick | Sq.m | 988 | 162
5.5.2 | 5.0 mm thick | Sq.m | 1141 | 187
5.5.3 | 6.0 mm thick | Sq.m | 1277 | 209
5.5.4 | 8.0 mm thick | Sq.m | 1642 | 269
5.5.5 | 10.0 mm thick | Sq.m | 2190 | 359
5.5.6 | 16.0 mm thick | Sq.m | 3467 | 568
5.5.7 | 20.0 mm thick | Sq.m | 5419 | 888
5.6 | P & F phenolic laminated sheet 2.0 mm thick of following size . Including screws, cup washer as required.
5.6.1 | 75 mm dia | Each | 11 | 2
5.6.2 | 100 mm dia. | Each | 16 | 3
5.7 | P & F P.V.C. sheet 2.0 mm thick of following size Including screws, cup washer as required.
5.7.1 | 75 mm dia. | Each | 6 | 1
5.7.2 | 100 mm dia. | Each | 7 | 1
5.8 | P & F Aluminium sheet 1.0 m thick of following size dia. Including screws, cup washer as required.
5.8.1 | 75 mm dia. | Each | 10 | 2
5.8.2 | 100 mm dia. | Each | 12 | 2
5.9 | P & F 1.2 mm thick M.S. Recessed concealed box, round of size 150 mm dia, depth 100 mm complete as required. | Each | 95 | 16
5.10. | Labour charges for dismantling of surface PVC/ Steel conduit including wiring in conduit, conduit fittings and depositing the same with listing of material in store. | Mtr. |  | 11
5.11 | Labour charges for dismantling of surface/ recessed switch board of any size and depositing the same with listing of material in store. | Each |  | 9
5.12 | Labour charges for dismantling of switch accessories like switch, socket, ceiling rose, holder and depositing the same with listing of material in store. | Each |  | 4
5.13 | Labour charges for dismantling of wiring in existing conduit of following size and depositing the same with listing of material in store.
5.13.1 | up to 2.5 sq. mm. wire | Mtr. |  | 2
5.13.2 | 4/ 6 sq. mm. wire | Mtr. |  | 4
5.13.3 | 10 sq. mm. wire | Mtr. |  | 6

## Ch 6 DB & Accessories
Chapter E - 06
Distribution Board & it's Accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
6.1 | Providing & Fixing of 240/415 V AC MCB with positive isolation of 10 kA breaking capacity (B/ C/D tripping characteristic as per type of load and site requirement) 4 KV impulse withstand voltage, ISI marked IS 8828(1996) / conforming to IEC 60898-1 2002, IEC 60947-2, low watt losses, trip free mechanism , energy limiting of class 3 as per IEC, minimum phase termination capacity of 25 sq.mm., conductor line load reversibility , IP 20 contact protection and fitted in existing distribution board/sheets, minimum electrical operation 20,000 upto 20 A rating, 10,000 upto 63 A, 5000 for 80 A & above rating including making connections, testing etc. as required.
6.1.1 | Single pole MCB (With B / C curve tripping characteristics)
6.1.1.1 | 0.5 A to 5 A rating | Each | 278 | 17
6.1.1.2 | 6 A to 32 A rating | Each | 169 | 17
6.1.1.3 | 40 A rating | Each | 390 | 22
6.1.1.4 | 50/63 A rating | Each | 395 | 28
6.1.1.5 | 80 A rating | Each | 1522 | 33
6.1.1.6 | 100 A rating | Each | 1706 | 39
6.1.1.7 | 125 A rating | Each | 1849 | 56
6.1.2 | Double pole MCB (With B / C curve tripping characteristics)
6.1.2.1 | 0.5 A to 5 A rating | Each | 772 | 28
6.1.2.2 | 6 A to 32 A rating | Each | 561 | 28
6.1.2.3 | 40 A rating | Each | 899 | 39
6.1.2.4 | 50/63 A rating | Each | 910 | 50
6.1.2.5 | 80 A rating | Each | 3360 | 61
6.1.2.6 | 100 A rating | Each | 3591 | 72
6.1.2.7 | 125 A rating | Each | 3979 | 105
6.1.3 | Triple pole MCB (With B / C curve tripping characteristics)
6.1.3.1 | 0.5A to 5 A rating | Each | 1127 | 44
6.1.3.2 | 6 A to 32 A rating | Each | 884 | 44
6.1.3.3 | 40 A rating | Each | 1358 | 61
6.1.3.4 | 50/63 A rating | Each | 1374 | 78
6.1.3.5 | 80 A rating | Each | 5300 | 94
6.1.3.6 | 100 A rating | Each | 5663 | 111
6.1.3.7 | 125 A rating | Each | 6325 | 167
6.1.4 | Four pole MCB (With B / C curve tripping characteristics)
6.1.4.1 | 0.5A to 5 A rating | Each | 1418 | 56
6.1.4.2 | 6 A to 32 A rating | Each | 1206 | 56
6.1.4.3 | 40 A rating | Each | 1715 | 83
6.1.4.4 | 50/63 A rating | Each | 1737 | 105
6.1.4.5 | 80 A rating | Each | 6926 | 128
6.1.4.6 | 100 A rating | Each | 7237 | 167
6.1.4.7 | 125 A rating | Each | 8218 | 211
6.1.5 | Triple pole MCB (With D curve tripping Characteristics)
6.1.5.1 | 0.5 A to 5 A rating | Each | 1143 | 54
6.1.5.2 | 6 A to 32 A rating | Each | 921 | 43
6.1.5.3 | 40 A rating | Each | 1418 | 66
6.1.5.4 | 50/63 A rating | Each | 1435 | 66
6.2 | Providing & Fixing of 240/415 V isolator ISI marked IS:13947-III/conforming to IEC 60947-3, suitable for AC22A utilization catagory, 4KV impulse withstand voltage, true contact indication, Red colour dolly / lever shall have single mould covering over all poles for operation , two position din rail mounting, minimum phase termination capacity of 25sq.mm. IP 20 contact protection and fitted in existing distribution board / sheet including making connections, testing etc. as required.
6.2.1 | Double pole isolator
6.2.1.1 | 30 A / 40 A rating | Each | 340 | 39
6.2.1.2 | 63 A rating | Each | 467 | 49.995
6.2.1.3 | 80 A/100 A rating | Each | 621 | 67
6.2.2 | Triple pole Isolator
6.2.2.1 | 40 A rating | Each | 627 | 61
6.2.2.2 | 63 A rating | Each | 737 | 78
6.2.2.3 | 80 A/100 A rating | Each | 869 | 100
6.2.3 | Four pole Isolator
6.2.3.1 | 40 A rating | Each | 814 | 83
6.2.3.2 | 63 A rating | Each | 869 | 105
6.2.3.3 | 80 A/100 A rating | Each | 1065 | 139
6.3 | Providing & Fixing of 240/415 V factory fitted RCBO with overload, short-circuit and earth leakage protection with ISI marked (IS12640-2)/ conforming to IEC 61009-1, breaking capacity 10 KA, provision for pad lock, min. Electrical operation 10,000 upto 63 A rating , minimum phase termination capacity of 25 sq.mm. , IP 20 contact protection with existing distribution board / sheet including making connections, testing etc. as required.
6.3.1 | Two pole 30 mA sensitivity
6.3.1.1 | 6A-32 A rating | Each | 2791 | 56
6.3.1.2 | 40 A rating | Each | 2819 | 83
6.3.1.3 | 63 A rating | Each | 3374 | 111
6.3.2 | Two pole 100/300mA sensitivity
6.3.2.1 | 6A-32 A rating | Each | 2882 | 56
6.3.2.2 | 40 A rating | Each | 2910 | 83
6.3.2.3 | 63 A rating | Each | 3600 | 111
6.3.3 | Four pole 30 mA sensitivity
6.3.3.1 | 6A-32 A rating | Each | 3157 | 111
6.3.3.2 | 40 A rating | Each | 3262 | 167
6.3.3.3 | 63 A rating | Each | 3931 | 222
6.3.4 | Four pole 100/300 mA sensitivity
6.3.4.1 | 6A-32 A rating | Each | 3471 | 111
6.3.4.2 | 40 A rating | Each | 3537 | 167
6.3.4.3 | 63 A rating | Each | 3999 | 222
6.4 | P&F 240/415 V AC Change Over Miniature circuit breaker with three positions (I-O-II) which allows supply change over from one source to second source & vice- versa, conforming to IS/ IEC 60947-3 in existing board/sheets including making connections, testing etc. as required.
6.4.1 | Double Pole
6.4.1.1 | 25 Amp, 2 Module | Each | 994.9984 | 56
6.4.1.2 | 40 Amp, 2 Module | Each | 1520 | 83
6.4.1.3 | 63 Amp,3 Module | Each | 1784 | 111
6.4.2 | FourPole
6.4.2.1 | 40 Amp, 4 Module | Each | 2586 | 121
6.4.2.2 | 63 Amp, 6 Module | Each | 2974 | 138
6.5 | Providing & Fixing of 240/415 V Residual current circuit breaker (RCCB) conforming to (IS:12640-1)/ IEC 61008 -1 , rated 4 KV impulse withstand voltage truly current operated and shall operate on CBCT mechanisum, provision for pad lock, min. Electrical operation 10,000 upto 63 A rating and 5000 for 100 A rating and minimum phase termination capacity of 25 sq.mm. rigid wire , IP 20 contact protection with existing distribution board / sheet including making connections, testing etc. as required.
6.5.1 | Two pole 30 mA sensitivity
6.5.1.1 | 16/25 A rating | Each | 1877 | 56
6.5.1.2 | 32/40 A rating | Each | 2130 | 83
6.5.1.3 | 63A rating | Each | 2660 | 111
6.5.1.4 | 100 A rating | Each | 4617 | 167
6.5.2 | Two pole 100/300mA sensitivity
6.5.2.1 | 16/25 A rating | Each | 1948 | 56
6.5.2.2 | 40 A rating | Each | 2248 | 83
6.5.2.3 | 63 A rating | Each | 2723 | 111
6.5.3 | Four pole 30 mA sensitivity
6.5.3.1 | 25 A rating | Each | 2495 | 111
6.5.3.2 | 40 A rating | Each | 2517 | 111
6.5.3.3 | 63 A rating | Each | 2856 | 133
6.5.3.4 | 100 A rating | Each | 4833 | 133
6.5.4 | Four pole 100/300 mA sensitivity
6.5.4.1 | 25 A rating | Each | 2559 | 111
6.5.4.2 | 40 A rating | Each | 2600 | 111
6.5.4.3 | 63 A rating | Each | 2987 | 133
6.5.4.4 | 100 A rating | Each | 4913 | 133
6.6 | Providing & Fixing of din rail mounting surge protection device confirming to IEC 61643-11 for Type 1 + 2 protection and Maximum discharge current 50 kA with following configuration in existing distribution board / sheet including making connections, testing etc. as required.
6.6.1 | 1P + N | Each | 6015 | 222
6.6.2 | 3P + N | Each | 11539 | 444
6.7 | Providing & Fixing of din rail mounting contactor and accessories confirming to IEC 61095 with following description and configuration in existing distribution board / sheet including making connections, testing etc. as required.
6.7.1 | Modular contactor 25A - 1NO | Each | 1099 | 56
6.7.2 | Modular contactor 25A - 2NO | Each | 1374 | 67
6.7.3 | Modular contactor 40A - 2NO | Each | 2350 | 111
6.7.4 | Modular contactor 40A - 3NO | Each | 3364 | 156
6.7.5 | Modular contactor 40A - 4NO | Each | 3947 | 183
6.7.6 | Modular contactor 63A - 2NO + 2 NC | Each | 4172 | 194
6.7.7 | Modular contactor 63A - 3NO | Each | 4276 | 200
6.7.8 | Modular contactor 63A - 4NO | Each | 4711 | 222
6.7.9 | Auxilary contact, 2 NO | Each | 1023 | 50
6.7.10 | Auxilary contact, 1 NO + 1 NC | Each | 619 | 67
6.7.11 | Under voltage Release | Each | 1372 | 64
6.7.12 | Shunt Trip Release | Each | 1574 | 74
6.8 | Providing & Fixing of din rail mounting LED Indicating Lights with following description and configuration in existing distribution board / sheet including making connections, testing etc. as required.
6.8.1 | Red / Yellow / Blue / Green | Each | 640 | 33
6.8.2 | Red-yellow-Blue | Each | 772 | 33
6.9 | Providing & Fixing of Recessed/surface mounting heavy duty Enclosure made out from Galvanized steel / CRCA sheet, powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3. complete with din rail making internal DB terminations with copper lugs, detachable gland plate, including making connections, testing etc. as required.
6.9.1 | Suitable for Two / Three / Four module for MCB | Each | 580 | 56
6.9.2 | Suitable for Six / Eight module for MCB/ RCCB | Each | 1010 | 72
6.10. | Providing & Fixing of Recessed/surface mounting heavy duty horizontal type Double Door (Metal / Glazed / Acrylic) Distribution board with Metal end box made out from Galvanized steel / CRCA sheet, powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3, complete with 100 amp. insulated copper bus bar/shorting link , brass neutral link with shrouds, brass earth link , door earthing arrangement, color coded interconnecting wire set of minimum 10.0 sqmm size and din bar,masking sheet, making internal DB terminations with copper lugs, Ferrules, detachable gland plate, including making connections, testing etc. as required.
6.10.1 | Metal door (single phase) IK-09 and IP-43 with Metal end box
6.10.1.1 | 4 Way | Each | 1807 | 84
6.10.1.2 | 6 Way | Each | 2001 | 93
6.10.1.3 | 8 Way | Each | 2312 | 108
6.10.1.4 | 12 Way | Each | 2718 | 127
6.10.1.5 | 16 Way | Each | 3202 | 150
6.10.2 | Glazed / Acrylic door (single phase) IK-09 and IP-43 with Metal end box
6.10.2.1 | 4 Way | Each | 2159 | 101
6.10.2.2 | 6 Way | Each | 2404 | 112
6.10.2.3 | 8 Way | Each | 2870 | 134
6.10.2.4 | 12 Way | Each | 3546 | 166
6.10.2.5 | 16 Way | Each | 3872 | 181
6.10.3 | Metal door (Three phase) IK-09 and IP-43 with Metal end box
6.10.3.1 | 4 Way (8 incomer + 12 Outgoing) | Each | 3853 | 180
6.10.3.2 | 6 Way (8 incomer + 18 Outgoing) | Each | 4784 | 224
6.10.3.3 | 8 Way (8 incomer + 24 Outgoing) | Each | 5752 | 269
6.10.3.4 | 12 Way (8 incomer + 36 Outgoing) | Each | 8256 | 386
6.10.4 | Glazed / Acrylic door (Three phase) IK-09 and IP-43 with Metal end box
6.10.4.1 | 4 Way (8 incomer + 12 Outgoing) | Each | 4962 | 232
6.10.4.2 | 6 Way (8 incomer + 18 Outgoing) | Each | 6045 | 283
6.10.4.3 | 8 Way (8 incomer + 24 Outgoing) | Each | 7189 | 336
6.10.4.4 | 12 Way (8 incomer + 36 Outgoing) | Each | 10660 | 498
6.10.5 | Metal door (Three phase) Per phase isolation, Horizontal IK-09 and IP-43 with Metal end box
6.10.5.1 | 4Way {8 Incomer + 6 Sub Incomer (2+2+2) + 12 out going } | Each | 6311 | 295
6.10.5.2 | 6Way {8 Incomer + 6 Sub Incomer (2+2+2) + 18 out going } | Each | 7500 | 351
6.10.5.3 | 8Way. {8 Incomer + 6 Sub Incomer (2+2+2) + 24 out going } | Each | 9005 | 421
6.10.5.4 | 12 Way {8 Incomer + 6 Sub Incomer (2+2+2) + 36 out going } | Each | 12200 | 570
6.11 | Providing & Fixing of Recessed/surface mounting heavy duty Flexi / Row type Distribution board with Metal end box made out from Galvanized steel / CRCA sheet , powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3 complete with 100 Amp. copper shorting link , brass neutral link with shrouds, brass earth link , color coded interconnecting wire set of suitable rating and din bar, door earthing arrangement, masking sheet, making internal DB terminations with copper lugs, ferrules detachable gland plate, including making connections, testing etc. as required.
6.11.1 | Double door IK-09 & IP-43 with metal End box
6.11.1.1 | 4 Row 32 Module(8 module per row) | Each | 5655 | 264
6.11.1.2 | 4 Row 40 Module(10 module per row) | Each | 5946 | 325
6.11.1.3 | 4 Row 56 Module(14 module per row) | Each | 6699 | 313
6.11.1.4 | 3 Row 42 Module(14 module per row) with provision of 160 Amp. MCCB | Each | 6946 | 325
6.11.2 | Glazed / Acrylic door IK-09 & IP-43 with Metal End Box
6.11.2.1 | 4 Row 32 Module(8 module per row) | Each | 5522 | 258
6.11.2.2 | 4 Row 40 Module(10 module per row) | Each | 5950 | 578
6.11.2.3 | 4 Row 56 Module(14 module per row) | Each | 7479 | 350
6.12 | P&F metal clad / Polyamide industrial plug top & socket unit with pin and sleeve type contact on porcelain/ bakelite base in Recessed/surface mounting heavy duty Enclosure made out from Galvanized steel / CRCA sheet , powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3. (without MCB) including making connections, testing etc.as required.
6.12.1 | 20 amp, (2P + E), 1 Module | Each | 1458 | 68
6.12.2 | 20 amp, (2P + E), 2 Module | Each | 1570 | 73
6.12.3 | 20 amp, (2P + E), 3 Module | Each | 2971 | 139
6.12.4 | 32 amp, (3P + E), 3 Module | Each | 3335 | 156
6.12.5 | 32 amp, (3P + N + E) 8 Module (with Polyamide Plug & Socket) | Each | 4329 | 202
6.12.6 | 63 amp, (3P + N+ E), 8 Module (with Polyamide Plug & Socket) | Each | 11841 | 553
6.13 | P & F of Industrial plug and socket conforming to IEC 60309-1/2 made out of self extinguishing engineering polymer / polyamide, nickel plated brass sleeve and pins, socket with shutter including making connection etc as reqd.
6.13.1 | IP -67, IK - 09 Panel mounted socket
6.13.1.1 | 16 A (2P+E) |  | 779 | 36
6.13.1.2 | 32 A (2P+E) | Each | 961 | 45
6.13.1.3 | 32 A (3P+N+E) | Each | 1109 | 52
6.13.1.4 | 63 A (3P+N+E) | Each | 3459 | 162
6.13.2 | IP -67, IK-09 Surface/Wall mounted socket
6.13.2.1 | 16 A (2P+E) | Each | 1031 | 48
6.13.2.2 | 32 A (2P+E) | Each | 1285 | 60
6.13.2.3 | 32 A (3P+N+E) | Each | 2253 | 221
6.13.2.4 | 63 A (3P+N+E) | Each | 4726 | 221
6.13.3 | IP -66, Surface/Wall mounted Interlocked switched socket Outlet with Provision of MCB
6.13.3.1 | 16 A (2P+E) 250 V | Each | 7128 | 333
6.13.3.2 | 32 A (2P+E), 250 V | Each | 8317 | 389
6.13.3.3 | 32 A (3P+E), 415 V | Each | 9287 | 434
6.13.3.4 | 32 A (3P+N +E), 415 V | Each | 10119 | 473
6.13.3.5 | 63 A (3P+N +E), 415 V | Each | 21429 | 1001
6.13.4 | IP - 67 Plug top
6.13.4.1 | 16 A (2P+E) | Each | 739 | 34
6.13.4.2 | 32 A (2P+E) | Each | 1037 | 48
6.13.4.3 | 32 A (3P+E) | Each | 1079 | 50
6.13.4.4 | 32 A (3P+N+E) | Each | 1256 | 59
6.13.4.5 | 63 A (3P+N+E) | Each | 3342 | 156
6.14 | Providing & Fixing of Recessed/surface mounting heavy duty Vertical TPN Distribution board with Metal end box with provision of incomer suitable for MCB / RCCB/ RCBO up to 63 Amp and SP / TP MCB upto 32 Amp. as outgoing ,made out from Galvanized steel / CRCA sheet, powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3 complete with insulated 100 A rating copper bus bar, brass neutral bars with shrouds, brass earth bar , color coded interconnecting wire set of suitable rating and din bar, door earthing arrangement, masking sheet, making internal DB terminations with copper lugs, ferrules, detachable gland plate, including making connections, testing etc. as required.
6.14.1 | Double door IK-09 & IP-43 with Metal end box
6.14.1.1 | 4 Way (8 Incomer +12 Outgoing) | Each | 8950 | 418
6.14.1.2 | 6 Way (8 Incomer +18 Outgoing) | Each | 9838 | 460
6.14.1.3 | 8 Way (8 Incomer +24 Outgoing) | Each | 11232 | 525
6.14.1.4 | 12 Way (8 Incomer + 36 Outgoing) | Each | 14743 | 689
6.15 | Providing & Fixing of Recessed/surface mounting heavy duty Vertical TPN Distribution board with Metal end box with provision of incomer suitable for 3/4 pole MCCB and SP / TP MCB up to 63 Amps. as outgoing ,made out from Galvanized steel / CRCA sheet , powder coated conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3. complete with insulated 125/160/200/250 Amp. copper bus bar, brass neutral bars with shrouds, brass earth bar , color coded interconnecting wire set of suitable rating and din bar, door earthing arrangement, masking sheet, making internal DB terminations with copper lugs, ferrules, detachable gland plate, including making connections, testing etc. as required.
6.15.1 | Double door IP-43 & IK-09 with Provision of Incomer MCCB up to 125 A Rating with Metal end box
6.15.1.1 | 4 Way | Each | 10372 | 485
6.15.1.2 | 6 Way | Each | 11630 | 543
6.15.1.3 | 8 Way | Each | 12684 | 593
6.15.1.4 | 12 Way | Each | 16834 | 787
6.15.2 | Double door IP-43 & IK-09 with Provision of Incomer MCCB 160 A Rating with Metal End Box
6.15.2.1 | 4 Way | Each | 13127 | 613
6.15.2.2 | 6 Way | Each | 14561 | 680
6.15.2.3 | 8 Way | Each | 15898 | 743
6.15.2.4 | 12 Way | Each | 18996 | 888
6.15.3 | Double door IP-43 & IK-09 with Provision of Incomer MCCB 200/250 A Rating with metal End Box
6.15.3.1 | 4 Way | Each | 14643 | 684
6.15.3.2 | 6 Way | Each | 16380 | 765
6.15.3.3 | 8 Way | Each | 18323 | 856
6.15.3.4 | 12 Way | Each | 21421 | 1001
6.16 | P & F Surface mounting IP-65, IK-09 Class-II self extinguishing insulating material weather proof cabinets confirming to EN60439-3 with IP-65 Key lock, fully reversible door and cabinet, removable chasis and face plates, of following size.
6.16.1 | 3/4 module | Each | 2241 | 105
6.16.2 | 6 module | Each | 2784 | 130
6.16.3 | 8 module | Each | 4599 | 215
6.16.4 | 1 row 12 module | Each | 5476 | 256
6.16.5 | 2 row 24 module | Each | 6240 | 292
6.16.6 | 3 row 36 module | Each | 7777 | 363
Note:
1 | To ensure single point responsibility, Distribution Board and it's associate switchgear like MCB, MCCB, Isolator, RCCB etc. should be of same make.
2 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 7 Electrical Accessories
Chapter E - 07
Electrical Wiring Accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
7.1 | P & F ISI marked (IS:3854) 6 amp. flush type non modular switch with CM/L no. printed and made out from industrial grade Polycarbonate material including cutting hole in tile and making connection testing etc. as required. | Each | 21 | 1
7.2 | P & F ISI marked (IS :3854) 16 amp. flush type non modular switch CM/L no. printed and made out from industrial grade Polycarbonate material including cutting hole in tile and making connection testing etc. as required. | Each | 48 | 2
7.3 | Providing & Fixing of 6 amp. Combined flush type non modular socket and switch set made out from industrial grade Polycarbonate material including cutting hole in tile and making connection testing etc. as required. | Each | 117 | 5
7.4 | Providing & Fixing of 16 amp. Combined flush type non modular socket and switch set with indicator and fuse set, made out from industrial grade Polycarbonate material including cutting hole in tile and making connection testing etc. as required. | Each | 173 | 8
7.5 | Providing & Fixing of ISI marked (IS :3854) non modular 6A bell push surface type CM/L no. printed and made out from industrial grade Polycarbonate material including making connection testing etc. as required. | Each | 30 | 1
7.6 | Providing & Fixing of ISI marked (IS :3854) twin control non modular 6A switch surface type, CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal & captive screws including making connection testing etc. as required. | Each | 44 | 2
7.7 | Providing & Fixing of ISI marked (IS :3854) non modular 6A bell push flush type CM/L no. printed and made out from industrial grade Polycarbonate materialincluding cutting hole in tile and making connection testing etc. as required. | Each | 30 | 1
7.8 | Providing & Fixing of ISI marked (IS :3854) twin control non modular 6A switch flush type CM/L no. printed , made out from industrial grade Polycarbonate material, including cutting hole in tile and making connection testing etc. as required. | Each | 26 | 1
7.9 | Providing & Fixing of non modular 6A hanging bell push/one way switch made out from industrial grade Polycarbonate material including making connection testing etc. as required. | Each | 34 | 2
7.10 | Providing & Fixing of IS:1293 marked of 3 pin 6 amp. flush type non modular socket CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal with Porcelain based back cover & captive screws including cutting hole in tile and making connection testing etc. as required. | Each | 28 | 1
7.11 | Providing & Fixing of IS:1293 3/6 pin 16 amp flush type non modular socket CM/L no. printed and made out from Industrial grade Polycarbonate material, brass terminal with Porcelain based back cover & captive screws including cutting hole in tile and making connection testing etc. as required. | Each | 73 | 3
7.12 | Providing & Fixing of ISI marked (IS:371) 6 amp surface type 3 pin ceiling rose with CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal & captive screws including making connection testing etc. as required. | Each | 28 | 1
7.13 | Providing & Fixing of ISI marked (IS:1258) batten/angle lamp holder with CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal & captive screws including making connection testing etc. as required. | Each | 28 | 1
7.14 | Providing & Fixing of ISI marked (IS:1293) 6 amp unbreakable 3 pin plug top having lamp indicator with CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal including making connection testing etc. as required. | Each | 41 | 2
7.15 | Providing & Fixing of ISI marked (IS:1293) 16 amp unbreakable 3 pin plug top having lamp indicator with CM/L no. printed and made out from industrial grade Polycarbonate material, brass terminal including making connection testing etc. as required. | Each | 66 | 3
7.16 | Providing & Fixing of flush type non modular 2 pin telephone socket with plug top made out from industrial grade Polycarbonate material, brass terminals including making connection testing etc. as required. | Each | 55 | 3
7.17 | Providing & Fixing of flush type non modular single line telephone jack made out from industrial grade Polycarbonate material, including making connection testing etc. as required. | Each | 69 | 3
7.18 | Providing & Fixing of flush type non modular double line telephone jack made out from industrial grade Polycarbonate materialincluding making connection testing etc. as required. | Each | 81 | 4
7.19 | Providing & Fixing of flush type non modular coaxial T.V. socket made out from industrial grade Polycarbonate material,including making connection testing etc. as required. | Each | 44 | 2
7.20 | Providing & Fixing of IS 11037 marked non modular socket size flush type 100 watt rotary minimum 5 step fan regulator with CM/L no. printed and made out from industrial grade Polycarbonate material including making connection testing etc. as required. | Each | 186 | 9
7.21 | P & F ISI marked 32 A D.P. switch with fuse and indicating lamp including making connection testing etc. as required. | Each | 160 | 7
7.22 | Providing & Fixing of ISI marked (IS:302) gong bell with CM/L no. printed including making connection testing etc. as required. | Each | 166 | 8
7.23 | Providing & Fixing of Non Modular Neon Light including making connection testing etc. as required. | Each | 104 | 5
7.24 | Providing & Fixing of single / multi tone electronic call bell / remote bell including making connection testing etc. as required. | Each | 480 | 22
7.25 | Providing & Fixing of ISI marked (IS:302) ding dong/musical chime bell including making connection testing etc. as required. | Each | 318 | 15
7.26 | Providing & Fixing of modular type switch/ bell push duly ISI marked (IS :3854) with CM/L no. printed and made out of unbreakable and fire retardant virgin UV Stabilized Polycarbonate with brass terminals and captive screws & silver alloy contact tip with IP-20 rating ,minimum width of switch toggle( PUSH PART ) should not less then 20mm, including making connections, testing etc as required.
7.26.1 | 6 A one way switch | Each | 35 | 2
7.26.2 | 6 A two way switch | Each | 47 | 2
7.26.3 | 6 A bell push | Each | 70 | 3
7.26.4 | 10 A one way switch | Each | 47 | 2
7.26.5 | 10 A two way switch | Each | 69 | 3
7.26.6 | 16 A one way switch 1M | Each | 84 | 4
7.26.7 | 20 A one way switch 1M | Each | 94 | 4
7.26.8 | 20 A one way switch 2M | Each | 139 | 6
7.26.9 | 16 Amp. 2 Module switch With Led Indicator | Each | 112 | 5
7.26.10 | 32 Amp. 2 Module switch With Led Indicator | Each | 162 | 8
7.27 | Providing & Fixing of IS:1293 marked modular type lockable feature socket with CM/L no. printed duly made out of unbreakable and fire retardant virgin poly carbonate with brass terminals and captive screws & silver alloy contact tip with IP-20 rating, including making connections, testing etc as required.
7.27.1 | 6 A 3 pin shuttered socket | Each | 84 | 4
7.27.2 | 6/16 A shuttered socket | Each | 144 | 7
7.27.3 | 13 A flat pin international socket (Non ISI) | Each | 200 | 9
7.28 | Providing & Fixing of modular type 100W Step Fan regulator duly ISI marked (IS 11037) with CM/L no. printed made out of unbreakable and fire retardant virgin poly carbonate with brass terminals and captive screws & silver alloy contact tip with IP-20 rating , including making connections, testing etc as required.
| 5 step fan regulator 2 Module | Each | 328 | 15
7.29 | Providing & Fixing of 3 M Key card switch with Load capacity 20 amp, Off time delay 30 Sec. made out of unbreakable and fire retardant virgin poly carbonate, including making connections, testing etc as required. | Each | 312 | 15
7.3 | Providing & Fixing of following modular accessories, made out of unbreakable and fire retardant virgin poly carbonate with brass terminals and captive screws & silver alloy contact tip with IP-20 rating, including making connections, testing etc as required.
7.30.1 | RJ-11 telephone jack single line | Each | 76 | 4
7.30.2 | RJ-11 telephone jack Double line | Each | 112 | 5
7.30.3 | USB Charger 2 A - 1 M with BIS mark | Each | 749 | 34.9965
7.30.4 | RJ-45, Cat 6 computer jack with shutter | Each | 394 | 18
7.30.5 | T.V. coaxial socket | Each | 84 | 4
7.30.6 | Blanking plate | Each | 17 | 1
7.30.7 | 25 Amp. 2 Module Motor Starter with on / off Push button | Each | 356 | 17
7.30.8 | LED Skirting /Foot Light 2 Module | Each | 397 | 18
7.30.9 | Electronic Chime/Buzzer 2M | Each | 210 | 10
7.30.10 | Modular MCB 6 A to 32 A SP | Each | 297 | 14
7.30.11 | Modular MCB 6 A to 32 A DP | Each | 564 | 26
7.31 | Providing & Fixing of following size mounting grid plates with cover plates made from fire retardent UV established high performance engineering plastic suitable for all universal metal boxes for front installation & removal direct fit type complete in all respect.
7.31.1 | 1/2 Module | Each | 62 | 3
7.31.2 | 3 Module | Each | 82 | 4
7.31.3 | 4 Module | Each | 91 | 4
7.31.4 | 5 Module | Each | 112 | 5
7.31.5 | 6 Module | Each | 131 | 6
7.31.6 | 8 Module | Each | 171.0046 | 8
7.31.7 | 10 Module | Each | 194 | 9
7.31.8 | 12 Module | Each | 205 | 10
7.31.9 | 16/18 Module | Each | 231 | 11
7.32 | Providing & Fixing of following size cover plates made from fire retardent UV established high performance engineering plastic suitable for all universal metal boxes for front installation & removal direct fit type complete in all respect.
7.32.1 | 1/2 Module | Each | 41 | 2
7.32.2 | 3 Module | Each | 57 | 3
7.32.3 | 4 Module | Each | 64 | 3
7.32.4 | 5 Module | Each | 69 | 3
7.32.5 | 6 Module | Each | 92 | 4
7.32.6 | 8 Module | Each | 120 | 6
7.32.7 | 10 Module | Each | 144 | 7
7.32.8 | 12 Module | Each | 146 | 7
7.32.9 | 16/18 Module | Each | 161 | 7
7.33 | Providing & Fixing of Hot dipped Galvanized metal box of 1.2 mm thick with earthing terminal and adjustable floating clamp in recess/ surface suitable for modular accessories as required.
7.33.1 | 1-2 Module | Each | 75 | 3
7.33.2 | 3 Module | Each | 110 | 5
7.33.3 | 4-5 Module | Each | 131 | 6
7.33.4 | 6-8 Module | Each | 210 | 10
7.33.5 | 10-12 Module | Each | 256 | 12
7.33.6 | 16/18 Module | Each | 325 | 15
7.34 | Providing & Fixing of Wiring Accessories OEM fabricated following size virgin material UPVC modular boxes on surface suitable for modular accessories as required.
7.34.1 | 1-2 Module | Each | 81 | 4
7.34.2 | 3 Module | Each | 99 | 5
7.34.3 | 4/5 Module | Each | 115 | 5
7.34.4 | 6 / 8 module | Each | 168 | 8
7.34.5 | 10 / 12 module | Each | 228 | 11
7.34.6 | 16/18 module | Each | 330 | 15
7.35 | Providing & Fixing of Multiple socket with surge and spikes protection cartridge not less then 5 KV with minimum four nos. universal 6 A sockets, one 6 A switch and 3 pin company fitted plug top and 3 core multistrand copper lead minimum 1.5 mtr. including making connection etc as required. | Each | 562 | 26
7.36 | Providing & Fixing of DLP PVC adaptable trunking system for cable management including finishing accessories like corners, tees, adjustable angles, junction etc. as required . The trunking system shall have adaptable system for modular type RJ 45 data socket/ wiring accessories/ power sockets and shall be covered with peal off plastic cover. OEM have to submit NABL accrediated /CPET lab test reports /EN 50085-2-1 complaince certificate.
7.36.1 | 80mm x 50mm | Mtr. | 976 | 19
7.36.2 | 100/105mm x 50mm | Mtr. | 1216 | 23
7.36.3 | 150/160mm x 50mm | Mtr. | 2125 | 41
7.36.4 | 195/200mm x 50mm | Mtr. | 2816 | 54
7.37 | Providing and fixing of power plug point with non modular accessories with Galvanized box of 1.2 mm thick with earth terminal with suitable size 3.0 mm thick phenolic laminated sheet (IS : 2036 - 1995) cover including cost of 16 amp. Switch (IS :3854) and 3/6 pin 16 amp. socket outlet making connection , testing , etc. as required. | Each | 248 | 22
7.38 | Supplying and fixing of power plug point with Modular accessories on hot dipped galvanized modular box of 1.2 mm thick with earthing terminal/connector on surface or in recessed with suitable size of modular face place with grid plate and cover plate including cost of ISI marked modular 16 amp. Switch (IS :3854) and 6/16 amp. socket outlet (IS:1293) making connection , testing , etc. as required. | Each | 460 | 41
7.39 | P & F Krone module with base frame in the recess / surface made out of 1.2 mm thick sheet steel box, front openable, having locking arrangements duly powder coated ,including dressing, ferruling and punching of telephone cable with krone tool etc. as required.
7.39.1 | 10 Pairs | Each | 791 | 71
7.39.2 | 20 Pairs | Each | 1006 | 90
7.39.3 | 50 Pairs | Each | 2155.7844 | 192.4808
7.39.4 | 100 Pairs | Each | 4312 | 385
7.39.5 | 200 Pairs | Each | 7186 | 642
7.4 | P & F Portable Residual Current Device (PRCD) 3 pin plug top 16 A, 30 mA sensitivity. Plug should have feature of power indicator, test button and reset function etc. as required. | Each | 1136 | 642
Note:
1 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 8 LT Panels
Chapter E - 08
LT Panels & Accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
8.1 | SITC of IP-42 and general construction confirming to IS:8623 : 1993, wall/ free standing floor mounted dust and vermin proof compartmentalised cubical panel as specifications and Other parameters required as per point (a) ,(b), (c),(d), (e), (f), (g), (h) as below:-
(a) Thickness of CRCA sheet shall not be less than 1.6 mm upto 450 mm length/ width of any compartment and be 2.0 mm above 450 mm, load bearing structure shall be 2.0 mm thick sheet supported by base M.S. channel if required, cable alley compartments having concealed hinged type doors with key type lock with / without detachable extension type structure. Removable 3 mm. thick sheet steel gland plates with appropriate size of knockouts for cables shall be provided
(b) complete panel shall undergo a process of degreasing, Water rinsing, Activation, derusting, pickling in acid bath, phosphatising & shall be subjected to nine tank process and then Powder coated with approved shade of minimum 70 microns on both side(Inner & Outer side) of panel. The panel having PE foam/ Neoprene rubber gasket of not less than 3mm thickness ,required hardware , concealed hinged door with key type locking arrangement for equipment/switchgear earthed with 2.5 sq.mm braided copper wire.
[c) Interconnection between bus bar and switchgears /cable shall be rigidly supported and made out by flexible copper wires (up to 63 amp ) and by solid bus bar (>63 amp ) . control wiring will be carried out with 1.5 Sq.mm, Earth wire with 2.5 Sq.mm and CT with 2.5 sq.mm flexible copper wire only. All joints / interconnections of copper bus bar shall be dully tinned . Clearance between main bus bar and risers / metal parts shall be at least 10 mm additional to width of bus bar Bus bar is insulated by Heat Shrinkable sleeves . Earth and Neutral bus bar shall be half of the size of phase bus bar. ( Cost of Bus bar / Flexible wire for Interconnection between Main busbar and Switchgear is to be Paid Extra )
(d) Wiring between components within switchgear and Incoming / outgoing cable shall be done through the terminal block only. Direct connection shall not be permitted. Each terminal block shall be one piece moulded, barrier type, 650 volt grade, complete with washers, heads, studs with two nuts and identification strips and shall have adequate continuous current rating. For tap-offs, adjacent terminals with shorting strips shall be used. 10% Spare terminal blocks shall be provided. Wire identification on marking strip shall correspond to the designation of the wiring diagrams. All wire terminals on the equipment shall also be marked with designation corresponding to those of the wiring diagram.
(e) All wiring shall be enclosed in plastic channels and neatly bunched and closed in metering chamber, Wiring between terminals of various devices shall be ‘point to point’ (no wire splitting or tee connections) with wires neatly trucked along the back of the panels, adequately supported to prevent sagging.
(f) Floor mounted panel shall be mounted on Base frame of ISMC channel size 100 x 50 x 5 mm ( to be paid Extra )
(g) Tests: The insulation resistance (with 1000 V Megger) and High voltage Power frequency test (by applying a voltage of 2.5KV for one minute) shall be measured between phases, between phase and neutral and between phase and earth. both before and after high voltage power frequency test. The insulation resistance shall not be less than three megaohm. CT Secondary current injection test shall also be carried out.
| (h) only outer surface area on all sides shall be measured & panel to be fabricated only from CPRI approved fabricator only (CPRI type Test certificates for Temp. rise test, Short circuit test for 50 kA and IP test is to be submitted) | Sqm. | 5575 | 498
8.2 | Supplying and fixing of Aluminium (IEC 60105 ISO 209-1,2) / Copper (IEC 60028) bus bar by means of SMC / DMC type insulator, with short circuit withstand capacity of 31 MVA for 1 Sec. , high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves.
8.2.1 | Electrolytic grade Aluminium bus bar 6010 grade | Kg. | 559 | 83
8.2.2 | Electrolytic grade (Cu+ETP) Tin Coated annealed copper bus bars IACS 100% grade. | Kg. | 1380 | 111
8.3 | Providing & Fixing of IS: 1248(part-1) 2003 confirming Moving Iron panel meter, 90 degree Analog type (up to 500) V range Volt meter / Direct- Ammeter / CT oertated ammeter of class 1.0 accuracy of size 96mm x 96 mm including making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required.
8.3.1 | Voltmeter ( 0 to 500V ) | Each | 716 | 64
8.3.2 | Ammeter (Direct Reading / CT Operated) | Each | 716 | 64
8.4 | Providing & Fixing of IS: 13875 & IEC :61326/IEC:62053-22 confirming LED Digital type (up to 500) V range Volt meter / Direct- Ammeter / CT opertated ammeter/ Frequency meter / KWH meter / Multi Function Meter / Power analyzer of class 1 accuracy of size 96mm x 96 mm including making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required.
8.4.1 | Single Phase Ammeter | Each | 1095.0016 | 98
8.4.2 | Single Phase Voltmeter | Each | 1095.0016 | 98
8.4.3 | Three phase Ammeter with Inbuilt Selector Switch | Each | 1506 | 134
8.4.4 | Three phase Voltmeter with Inbuilt Selector Switch | Each | 1506 | 134
8.4.5 | Three phase KWH Meter | Each | 3186 | 284
8.4.6 | Three phase KWH Meter Dual Source | Each | 3484 | 311
8.4.7 | Frequency Meter | Each | 1095 | 98
8.4.8 | Three phase AMP+HZ+PF+KW+KVA+KVAR+T.ENERGY+THD-I, THD-V & RUN HRS Meter | Each | 2932 | 262
8.4.9 | Three phase AMP + HZ + PF + KW + KVA + KVAR + KVARH+KWH+DUAL ENERGY+ ENERGY+THD-I, THD-V & RUN HRS Meter | Each | 4746 | 424
8.4.10 | Three phase with universal Auxiliary supply + AMP + HZ + PF + KW + KVA + KVAR + KVARH + KWH + DUAL ENERGY+ ENERGY+THD-I, THD-V & RUN HRS + MD with RS485 Meter | Each | 6869 | 613
8.5 | Providing & Fixing of Current Transformer confirming IS 2705-I (1992) with secondary terminal and shorting Block , with all necessary support in existing panel including connection etc. as required Current transformer Ring Type Tape Wound/Resin Cast Wound Accuracy Cl, CT ratio and burden as specified. ISF<=5, Cu cross section of secondary wire 1.5sqmm (minimum), including all necessary support in existing panel including connection etc. as required .
8.5.1 | Ring type tape wound CT
8.5.1.1 | C T Class 1, Ratio up to 150/5, Burden 5 VA | Each | 647 | 58
8.5.1.2 | C T Class 1, Ratio 200/5 to 600/5, Burden 10 VA | Each | 684 | 61
8.5.1.3 | C T Class 1, Ratio 800/5 to 1200/5, Burden 15 VA | Each | 1020 | 91
8.5.1.4 | C T Class 1, Ratio 1500/5 to 3000/5, Burden 15 VA | Each | 1643 | 147
8.5.1.5 | C T Class 1, Ratio 3200/5 to 5000/5, Burden 15 VA | Each | 2538 | 227
8.5.2 | Resin cast wound type CT
8.5.2.1 | C T Class 1, Ratio up to 150/5, Burden 5 VA | Each | 1294 | 116
8.5.2.2 | C T Class 1, Ratio 200/5 to 600/5, Burden 15 VA | Each | 1481 | 132
8.5.2.3 | C T Class 1, Ratio 800/5 to 1200/5, Burden 15 VA | Each | 2178 | 194
8.5.2.4 | C T Class 1, Ratio 1600/5 to 3000/5, Burden 15 VA | Each | 2489 | 222
8.5.2.5 | C T Class 1, Ratio 4000/5 to 5000/5, Burden 15 VA | Each | 4281 | 382
8.6 | Providing & Fixing of selector switch of 10 A for voltmeter using high grade engineering material to international standards with cam assembly insulation of glass filled polyamide with high tracking index. For reliable and stable electrical and mechanical endurance double butt contacts with silver bi-metal on copper should provided . contact assembly is of operating temp range 25 degree C to 55 degree C, frequency upto 10 KHz. Switch life under standard operating conditions shall be mechanically minimum 50000 operations @300 cycles/ hour and electrically 10,000 operations at 100% rated duty for 100 cycles/ hour including making connection etc. as required .
8.6.1 | Voltage Between Phases with OFF ( 4 Position ) | Each | 330 | 29
8.6.2 | Voltage Between Phases & Individual Phases to Neutral with OFF ( 7 Position ) | Each | 560 | 50
8.7 | Providing & Fixing of CT linked selector switch of 10 A for Ampere meter (4 position ) using high grade engineering material to international standards with cam assembly insulation of glass filled polyamide with high tracking index. For reliable and stable electrical and mechanical endurance double butt contacts with silver bi-metal on copper should provided . contact assembly is of operating temp range 25 degree C to 55 degree C, frequency upto 10 KHz. switch life under standard operating conditions shall be mechanically minimum 50000 operations @300 cycles/ hour and electrically 10,000 operations at 100% rated duty for 100 cycles/ hour , including making connection etc. as required . | Each | 348 | 31
8.8 | Providing & Fixing of 10 A Cam operated rotary (Local- Remote, Auto - manual) switches on existing panel with 1 pole 2 way and off position using high grade engineering material to international standards with cam assembly insulation of glass filled polyamide with high tracking index. For reliable and stable electrical and mechanical endurance double butt contacts with silver bi-metal on copper should provided . contact assembly is of operating temp range -25 degree C to 55 degree C, frequency upto 10 KHz. switch life under std. op. conditions shall be mechanically minimum 50000 operations @300 cycles/ hour and electrically 10,000 operations at 100% rated duty for 100 cycles/ hour including making connection etc. as required . | Each | 373 | 33
8.9 | Providing & Fixing of 25 A TNC ( Trip - neutal - close ) switch to control remotely on existing panel as required. | Each | 1387 | 124
8.10 | Providing & Fixing of 110/220 V, unibody LED Indicating lamp IEC 60947 with integral circuit, IP 65 above panel & IP 20 terminal block, Approx. body dia for panel not less then 20 mm, length min. 50mm, front LED cover dia min. 27 mm, contact material phospher bronze for Led, PCB contacts shall be of brass (tin plated), impulse dielectric tested for 2.5 KV, Rated insulation resistance shall be 100 M ohm at 500VDC including connection etc. as required.
8.10.1 | Red/yellow/Green colour | Each | 147 | 17
8.10.2 | Blue / white Colour | Each | 232 | 17
8.11 | Providing & Fixing of flush head push button actuators IEC 60947 with integral circuit, IP 65 above panel & IP 20 terminal block, Approx. body dia for panel not less then 20 mm, length min. 50mm, front LED cover dia min. 27 mm, contact material phospher bronze for Led, PCB contacts shall be of brass (tin plated), impulse dielectric tested for 2.5 KV, including connection etc. as required.
8.11.1 | Non luminous type | Each | 127 | 17
8.11.2 | Luminous type Red , Yellow, Green, Amber | Each | 266 | 17
8.11.3 | Luminous type Blue , white | Each | 470 | 17
8.12 | Providing & Fixing of Electrical insulating rubber matts confirming to IS: 15652 / 2006 with one side anti skid aberration marks and pasting the mat with synthetic rubber adhesive as required.
8.12.1 | 3.3 KV, class A 2 mm thick with proof voltage 10 KV AC (rms) and Break Down Voltage 30 KV AC (rms) | Sqm. | 1273 | 111
8.12.2 | 11 KV, Class B 2.5 mm thick with proof voltage 22 KV AC (rms) and Break Down Voltage 45 KV AC (rms) | Sqm. | 1754 | 111
8.12.3 | 33 KV, class C 3 mm thick with proof voltage 36 KV AC (rms) for 3 min. and Break Down Voltage 65 KV AC (rms) | Sqm. | 2072 | 111
8.13 | Providing & Fixing of self healing IP20 MPP type shunt capacitor (banks) conforming to IS:13340-41 / IEC :831-1&2 OR IEC : 60831-1& 2 in existing panel or parallel with load terminals , the capacitor shall be fitted with discharge resistors, pressure sensitive disconnector ( PSD ) and shall have dissipation factor less than 0.0025 at 50 Hz, Operating loss less than 0.30 Watt per KVAR. Min over current capacity 1.8 times rated current & peak inrush current min. 300 times of rated current, life expectancy greater than 100000hrs (temp class - 25 D) in 440 V including making connections, testing etc. as required.
8.13.1 | Heavy duty Three phase 440 V, 50 Hz cylindrical type capacitor (Bank) | KVAR | 334 | 22
8.13.2 | Heavy duty Three phase 525V, 50 Hz cylindrical type capacitor (Bank) | KVAR | 419 | 22
8.14 | Providing & Fixing of 3-Phase 415/440 V , 7 % / 14 % Detuned Reactors conforming to IEC 61558-2-20 & IEC 60076-6 Aluminium wound for harmonics filter with 180% to 200 % Linearity, H - Class Insulation ( 180 degree C), high temp. Disconnection above 155 deg C., ambient temperature: +60 deg C. with thermal cut off switch in existing panel with following Capacitor ratings. including making connections, testing etc. as required.
8.14.1 | 7 % (189 Hz) Aluminium wound Reactors
8.14.1.1 | For 1 to 5 KVAR capacitor | Each | 5343 | 667
8.14.1.2 | 10 KVAR | Each | 7472 | 889
8.14.1.3 | 12.5 KVAR | Each | 7870 | 1000
8.14.1.4 | 15 KVAR | Each | 9408 | 1111
8.14.1.5 | 20 KVAR | Each | 10819 | 1333
8.14.1.6 | 25 KVAR | Each | 11403 | 1666
8.14.1.7 | 50 KVAR | Each | 17999 | 2222
8.14.1.8 | 100 KVAR | Each | 34346 | 4444
8.14.2 | 14 % (133 Hz) Aluminium wound Reactors
8.14.2.1 | For 1 to 5 KVAR capacitor | Each | 7534 | 667
8.14.2.2 | 10 KVAR | Each | 10183 | 889
8.14.2.3 | 12.5 KVAR | Each | 10746 | 1000
8.14.2.4 | 15 KVAR | Each | 13776 | 1111
8.14.2.5 | 20 KVAR | Each | 15971 | 1333
8.14.2.6 | 25 KVAR | Each | 16824 | 1666
8.14.2.7 | 50 KVAR | Each | 23364 | 2222
8.14.2.8 | 100 KVAR | Each | 47002 | 4444
8.15 | Providing & Fixing of microprocessor based 3 CT’s for all 3 phase sensing compensation power factor correction relay with Approx. Size 139 mm x 139 mm, Operating Voltage 415/440 V , IEC / EN 61000-6-(2&4) having 3 CT sensing, sensitivity up to 50 milli amp secondary current , self analyzing auto c/k setting according to targeted power factor setting, the relay shall have digit display unit for display of real power factor, targeted power factor, lag/lead capacitor switching status, alarm output for under current, over current, High voltage, THD-I & THD-V insufficient compensation, communication interface with RS 485, indication of switching on units, auto/manual status, and shall have over load protection, no volt release , having multi Built in MFM with PF Controller LCD Display, CT polarity auto correction % THD up to 30 harmonics level, step switching time 2 sec to 1800 sec. Lead & Lag parameters, metering facility and 3 no. Class- 0.5 Cast Resin CT for sensing the relay including making connection with 1.5 Sq.mm copper wire etc. as required.
8.15.1 | 6 to 8 stage | Each | 16549 | 1478
8.15.2 | 12 to 16 stage | Each | 20842 | 1861
8.16 | Providing & Fixing of AC operated heavy duty 230 /440 Volt power contactor confirming to IS/IEC 60947-4-1 : 2000 having provision of mechanical interlocking, auxilary contacts, Din rail mounting type including making connections, testing etc. as required.
8.16.1 | 3 pole Power contactors with following AC 3 Rating
8.16.1.1 | Up to 12 Amp | Each | 961 | 86
8.16.1.2 | 16 to 25 Amp | Each | 1266 | 113
8.16.1.3 | 32 Amp. | Each | 2672 | 239
8.16.1.4 | 40 Amp | Each | 4042 | 361
8.16.1.5 | 50 Amp | Each | 4976 | 444
8.16.1.6 | 70 Amp | Each | 7085 | 633
8.16.1.7 | 80 Amp | Each | 8947 | 799
8.16.1.8 | 95 Amp | Each | 13171 | 1176
8.16.1.9 | 140 Amp | Each | 21265 | 1899
8.16.1.10 | 185 Amp | Each | 23846 | 2129
8.16.1.11 | 250 Amp | Each | 30394 | 2714
8.16.1.12 | 300 Amp | Each | 35515 | 3171
8.16.1.13 | 400 Amp | Each | 48430 | 4324
8.16.1.14 | 550 Amp | Each | 72016 | 6430
8.16.1.15 | 630 Amp | Each | 103898 | 9277
8.16.2 | 4 pole Power contactors with following AC 1 Rating
8.16.2.1 | 16 Amp. | Each | 1126 | 101
8.16.2.2 | 25/32 Amp. | Each | 1244 | 111
8.16.2.3 | 40 Amp | Each | 1653 | 148
8.16.2.4 | 50/55 Amp | Each | 2091 | 187
8.16.2.5 | 63 Amp | Each | 4300 | 384
8.16.2.6 | 100/105 Amp | Each | 8812 | 787
8.16.2.7 | 160 Amp | Each | 15039 | 1343
8.16.2.8 | 200 Amp | Each | 19262 | 1720
8.16.2.9 | 250 Amp | Each | 24648 | 2201
8.16.2.10 | 325 Amp | Each | 38972 | 3480
8.16.2.11 | 400 Amp | Each | 50375 | 4498
8.16.2.12 | 500 Amp | Each | 63659 | 5684
8.16.2.13 | 600 Amp | Each | 76197 | 6803
8.16.2.14 | 700 Amp | Each | 87078 | 7775
8.16.2.15 | 900 Amp | Each | 108256 | 9666
8.17 | Providing & Fixing of 440 Volt 3 pole capacitor (AC 6 B ) duty contactor with 3 no. early make and post break auxiliary contacts in series with quick discharge damping resistors/ reactors to limit the inrush current as per IS/IEC 60947-4-1 : 2000, insulation voltage 1000V, impulse withstand voltage 8 KV,Din rail mounting type including making connections, testing etc. as required. suitable for following capacity capacitor bank.
8.17.1 | up to 6 KVAR | Each | 1630 | 146
8.17.2 | 8.5 KVAR | Each | 2068 | 185
8.17.3 | 10 KVAR | Each | 2143 | 191
8.17.4 | 12.5 KVAR | Each | 2373 | 212
8.17.5 | 15.0 KVAR | Each | 2864 | 256
8.17.6 | 20.0 KVAR | Each | 3316 | 296
8.17.7 | 25.0 KVAR | Each | 3798 | 339
8.17.8 | 30.0 KVAR | Each | 5720 | 511
8.17.9 | 40.0 KVAR | Each | 9517 | 850
8.17.10 | 50.0 KVAR | Each | 10415 | 930
8.17.11 | 60.0 KVAR | Each | 12201 | 1089
8.17.12 | 75.0 KVAR | Each | 14014 | 1251
8.17.13 | 85 KVAR | Each | 14409 | 1287
8.17.14 | 100 KVAR | Each | 16238 | 1450
8.18 | P & F of Control relays (Auxiliary Contactor) for AC control standard. 24 V Coil 110, 240 V, 415 V, 50 Hz conforming to IS:13947-4-1/IEC:60947-4-1 with required NO & NC combination including making connections, testing etc. as required. | Each | 1369 | 122
8.19 | P & F of Front / Side mounting Add on Auxiliary Contact Block with required NO & NC combination including making connections, testing etc. as required. | Each | 697 | 62
8.20 | Providing & Fixing of thermal over load relay with built in single phase protection and having at least 1NO & 1NC contacts, manual /auto reset facility including making connection testing etc. as required.
8.20.1 | Up to 14 Amp | Each | 1212 | 108
8.20.2 | 14 to 23 Amp | Each | 1344 | 120
8.20.3 | 20 to 33 Amp | Each | 1680 | 150
8.20.4 | 24 to 40 Amp | Each | 2066 | 184
8.20.5 | 36 to 60 Amp | Each | 2750 | 246
8.20.6 | 45 to 75 Amp | Each | 3148 | 281
8.20.7 | 66 to 110 Amp | Each | 3653 | 326
8.21 | P & F of 240 / 415 V Electronic ON - OFF Timer 3 -30 Sec / 12 - 120 Sec including making Connection etc. as required. | Each | 2041 | 182
8.22 | Providing & Fixing of Electromechanical / digital time switch having following day / week programme and minimum 100 hours reserve and AC1 rating of 16-20 amperes including making connection, programming conforming to IEC 60730-1 and 60730-2-7 etc. as required.
8.22.1 | One day reserve (Electromechanical type ) | Each | 3900 | 500
8.22.2 | One day & week reserve (digital type ) | Each | 3497 | 448
8.23 | Providing & Fixing of 110 - 240 V, AC, 1 ph. , 2 W Astronomical time switch with surge suppressor, memory card, Sunrise / Sunset selectable, software for programming including making connection, etc. as required. | Each | 4992 | 640
8.24 | Providing & Fixing of IP54 direct or CT operated, 1x240 / 3x240 volts , 50 Hz static watt-hour meter (kwh) , having resolution 0.1 / 0.01 kwh , confirming to IS:13779/ IS:15959, LED indicators for tamper operation ( Reverse &/or earth connection) , pulsating LED indicator for meterology , LCD Display, cover plate for body and terminal sealing , push button for all standard parameters, including making connection ,testing etc. as required.
8.24.1 | up to 30 ampere single phase meter acc. Cl 1 | Each | 1430 | 183
8.24.2 | 10 A to 60 ampere Single phase meter acc. Cl 1 | Each | 1885 | 242
8.24.3 | 3ph, 4W KWh CT Operated Base mounting 240 V-/5A acc. Cl 0.5s | Each | 10529 | 1350
8.24.4 | 3ph, 4W KWh Direct Base mounting 240 V 10-60 Amp acc. Cl 1 | Each | 3224 | 413
8.24.5 | 3ph, 4W Trivector Meter,240 V(L-N) 5A acc. Cl 0.5 | Each | 15404 | 1975
8.25 | P & F of Automatic Transfer Switch (ATS) confirming to IEC60947-6-1, Utilization cateogory AC-33B with OEM fabricated enclosure for automatic on load transfer between two source power supply of 415V through Solenoid/Motorised mechanism and integrated with three positions realize fast transfer within 180 ms (for solenoid) and within 2.6 sec.(for motorised). ATS shall have three postions (S1-OFF-S2) , Manual / Auto Override feature, The two sources can be isolated in the off position with a padlock. capability to expand with RS 485 communication module, which can ensure real-time transmission of communication data. ATS shall have automatic generator start & stop control function; Auxillary contacts to indicate mechanical positions. Minimum Electrical operations 6000, of following Current ratings, including making connections etc. as required.
8.25.1 | 63 Amps | Each | 41187 | 3677
8.25.2 | 125 Amps | Each | 69570 | 6212
8.25.3 | 160 Amps | Each | 82530 | 7369
8.25.4 | 200 Amps | Each | 89393 | 7982
8.25.5 | 250 Amps | Each | 102101 | 9116
8.25.6 | 315 Amps | Each | 109157 | 9746
8.25.7 | 400 Amps | Each | 120933 | 10798
8.25.8 | 630 Amps | Each | 146820 | 13109
8.25.9 | 800 Amps | Each | 170634 | 15235
8.26 | P & F Earth leakage relay for continuous surveillance of the earth leakage current of Rating 240 VAC at 50/60 Hz, Overload : x2 continuously, x10 for 3 secs as per BS6253, Voltage Tolerance : : - 25% to +10% Operating temp.: : -10 C to +70 C, Setting of trip point : : 0.030, 0.10, 0.30, 0.50, 1.0 ,3.0 ,5.0, 10.0,20.0 & 30.0 ( User Selectable) with Alarm Relay Output, Trip Relay Output etc. as required.
8.26.1 | ELR with 35mm CBCT | Each | 2072 | 266
8.26.2 | ELR with 70mm CBCT | Each | 2254 | 289
8.26.3 | ELR with 120mm CBCT | Each | 2535 | 325
8.26.4 | ELR with 210mm CBCT | Each | 3367 | 432
8.27 | P & F of Direct on line (DOL) / Star - Delta Starter as per IEC type-2 Co-ordination chart of OEM in Existing Panel with circuit breaker having inbuilt overload protection or separate thermal Overload relay , Short circuit, phase loss protection, suitable Contactors, including wiring between switchgears, Indicating lamps for R,Y,B,ON,OFF, Push button for ON, OFF, Volt meter, Ammeter, selector switch for local/remote, auto/manual/OFF operation. Cast resin CT's, provision for potential free contacts making connection, testing etc. as required.
8.27.1 | Direct on line (DOL) Starter with following Motor rating
8.27.1.1 | Motor rating 0.55 KW | Set | 8816 | 1150
8.27.1.2 | Motor rating 0.75 KW | Set | 9933 | 1296
8.27.1.3 | Motor rating 1.5 KW | Set | 10184 | 1328
8.27.1.4 | Motor rating 2.2 KW | Set | 10214 | 1332
8.27.1.5 | Motor rating 4.0 KW | Set | 10882 | 1019
8.27.1.6 | Motor rating 5.5 KW | Set | 11298 | 1474
8.27.1.7 | Motor rating 7.5 KW | Set | 11579 | 1510
8.27.1.8 | Motor rating 9.0 KW | Set | 12156 | 1586
8.27.1.9 | Motor rating 11.0 KW | Set | 14438 | 1883
8.27.1.10 | Motor rating 15.0 KW | Set | 21590 | 2816
8.27.1.11 | Motor rating 18.5 KW | Set | 24348 | 3176
8.27.1.12 | Motor rating 22.0 KW | Set | 26883 | 3507
8.27.1.13 | Motor rating 30.0 KW | Set | 33350 | 4350
8.27.1.14 | Motor rating 37.0 KW | Set | 39451 | 5146
8.27.1.15 | Motor rating 45.0 KW | Set | 40755 | 5316
8.27.1.16 | Motor rating 55.0 KW | Set | 44196 | 5765
8.27.1.17 | Motor rating 75.0 KW | Set | 61647 | 8041
8.27.1.18 | Motor rating 90.0 KW | Set | 68902 | 8987
8.27.1.19 | Motor rating 110.0 KW | Set | 81633 | 10648
8.27.2 | Star - Delta Starter with following Motor rating
8.27.2.1 | Motor rating 4.0 KW | Set | 15749 | 2054
8.27.2.2 | Motor rating 5.5 KW | Set | 16316 | 2128
8.27.2.3 | Motor rating 7.5 KW | Set | 16643 | 2171
8.27.2.4 | Motor rating 9.0 KW | Set | 21352 | 2785
8.27.2.5 | Motor rating 11.0 KW | Set | 21970 | 2866
8.27.2.6 | Motor rating 15.0 KW | Set | 31753 | 4142
8.27.2.7 | Motor rating 18.5 KW | Set | 39746 | 5184
8.27.2.8 | Motor rating 22.0 KW | Set | 41455 | 5407
8.27.2.9 | Motor rating 30.0 KW | Set | 48394 | 6312
8.27.2.10 | Motor rating 37.0 KW | Set | 63398 | 8269
8.27.2.11 | Motor rating 45.0 KW | Set | 68201 | 8896
8.27.2.12 | Motor rating 55.0 KW | Set | 76024 | 9916
8.27.2.13 | Motor rating 75.0 KW | Set | 81229 | 10595
8.27.2.14 | Motor rating 90.0 KW | Set | 109636 | 14299
8.27.2.15 | Motor rating 110.0 KW | Set | 139036 | 18135
8.28 | SITC of IP-43 and general construction confirming to IEC 61439-1&2. type tested assembly (TTA) wall/ free standing floor mounted dust and vermin proof compartmentalised cubical panel as specifications and Other parameters required as per point (a) ,(b), (c),(d), (e), (f), (g), (h) as below:-
(a) Panel having short circuit withstand capacity of minimum of 50 kA for 1s (Icw rating) at 415 V, 50 HZ AC supply, Rated Impulse withstand voltage (Uimp) of 12kV for withstanding against transient Over voltage, mechanical impact level of IK10 level and internal arc for 50 kA for 0.3 second with aluminum busbar and fully type tested at an Independent Laboratory, Type test certificate has to be submitted for all rating of LV Switchgear to be used in Panel.
(b) All four Horizontal Busbars shall be in same compartment. Certified design of switchboards shall be proven design from OEM (Switchgear Manufacturer). OEM name should be mentioned on top of each column of switchboard. Also, OEM Partnership Certificate shall be furnished by Panel builder. Panel shall be fully modular with standard OEM designas per latest IEC 61439 Part 1&2 standard
© Panels and cubicles shall be fabricated with CRCA Sheet Steel of thickness, same as as per OEM Design. Sheet Steel having vibration free structure chemically treated with nine tank process before painting for surface treatment and powder coated, with suitable electrolytic grade high conductivity Aluminium busbar extensible type, busbar supports, ( Cost of Bus bar / Flexible wire for Interconnection between Main busbar and Switchgear is to be Paid Extra )
(d)Wiring between components within switchgear and Incoming / outgoing cable shall be done through the terminal block only. Direct connection shall not be permitted. Each terminal block shall be one piece moulded, barrier type, 650 volt grade, complete with washers, heads, studs with two nuts and identification strips and shall have adequate continuous current rating. For tap-offs, adjacent terminals with shorting strips shall be used. 10% Spare terminal blocks shall be provided. Wire identification on marking strip shall correspond to the designation of the wiring diagrams. All wire terminals on the equipment shall also be marked with designation corresponding to those of the wiring diagram.
(e)All wiring shall be enclosed in plastic channels and neatly bunched and closed in metering chamber, Wiring between terminals of various devices shall be ‘point to point’ (no wire splitting or tee connections) with wires neatly trucked along the back of the panels, adequately supported to prevent sagging.
(f)Floor mounted panel shall be mounted on Base frame of ISMC channel size 100 x 50 x 5 mm ( to be paid Extra )
(g) Tests: The insulation resistance (with 1000 V Megger) and High voltage Power frequency test (by applying a voltage of 2.5KV for one minute) shall be measured between phases, between phase and neutral and between phase and earth. both before and after high voltage power frequency test. The insulation resistance shall not be less than three megaohm. CT Secondary current injection test shall also be carried out.
| (h) only outer surface area on all sides shall be measured & panel to be fabricated only from Switchgear OEM approved fabricators only. Switchgear OEM Approval in Favour of Panel fabricator for confirmation of IEC 61439 -1&2 with type test certificates to be submitted. | Sqm. | 9395 | 839

## Ch 9 ACB MCCB
Chapter E 09
Air circuit breakers & MCCB
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
9.1 | SITC of Microprocessor based Draw out type 3/4 pole door interlock Air Circuit Breaker (ACB) as conforming to IS/IEC 60947 P - 2 :2003 in existing LT panel suitable for LT installation 440/415 V, 50 Hz and having adjustable over load, short-circuit, Instantaneous, earth fault (LSIG) with separate LED indication or Fault details on display for each type of fault shall confirm to EMI/ EMC test , LCD/LED display, last 10 trip history, Inbuilt ZSI, Current metering, Provision for Communication, Thermal memory, trip free mechanism, modular design and suitable for ambient 50 degree and utilization catagary B. In built electrical & mechanical anti pumping feature , pollution degree 3, 100% rated neutral . ACB shall have separate indication for service, test, isolation & maintenance position, Breaking capacity Icu = Ics = Icw ( 1 sec ) , U imp - 12 KV, break time not more then 30 ms. Provision for electrical & mechanical interlock between ACB sand other required accessories (Cost of accessories to be paid extra) Min.electrical operation 10000 upto 1600 A rating and 5000 for 2000 A to 4000 A. including making connections, testing etc. as required. OEM shall have submit NABL / CPRI / ERDA/ Intertek accrediated lab type test certificate.
9.1.1 | Manual spring charged type 3 Pole
9.1.1.1 | 630/800 A Rating , 50 kA | Each | 120811 | 10787
9.1.1.2 | 1000 A Rating , 50 kA | Each | 126496 | 11294
9.1.1.3 | 1250 A Rating ,50 kA | Each | 140934 | 12583
9.1.1.4 | 1600 A Rating ,50 kA | Each | 155323 | 13868
9.1.1.5 | 2000 A Rating ,50 kA | Each | 190272 | 16989
9.1.1.6 | 2500 A Rating ,50 kA | Each | 229848 | 20522
9.1.1.7 | 3200 A Rating ,65 kA | Each | 293859 | 26237
9.1.1.8 | 4000 A Rating ,65 kA | Each | 376365 | 33604
9.1.2 | Motorised charged type 3 Pole
9.1.2.1 | 630/800 A Rating , 50 kA | Each | 148316 | 13243
9.1.2.2 | 1000 A Rating , 50 kA | Each | 153993 | 13749
9.1.2.3 | 1250 A Rating ,50 kA | Each | 163641 | 14611
9.1.2.4 | 1600 A Rating ,50 kA | Each | 190969 | 17051
9.1.2.5 | 2000 A Rating ,50 kA | Each | 222651 | 19880
9.1.2.6 | 2500 A Rating ,50 kA | Each | 256029 | 22860
9.1.2.7 | 3200 A Rating ,65 kA | Each | 322490 | 34193
9.1.2.8 | 4000 A Rating ,65 kA | Each | 152062 | 13577
9.1.3 | Manual spring charged type 4 Pole
9.1.3.1 | 630/800 A Rating , 50 kA | Each | 152062 | 13577
9.1.3.2 | 1000 A Rating , 50 kA | Each | 155456 | 13880.0185
9.1.3.3 | 1250 A Rating ,50 kA | Each | 183391 | 16374
9.1.3.4 | 1600 A Rating ,50 kA | Each | 199887 | 17847
9.1.3.5 | 2000 A Rating ,50 kA | Each | 247161 | 22068
9.1.3.6 | 2500 A Rating ,50 kA | Each | 295739 | 26405
9.1.3.7 | 3200 A Rating ,65 kA | Each | 358255 | 31987
9.1.3.8 | 4000 A Rating ,65 kA | Each | 504951 | 45085
9.1.4 | Motorised charged type 4 Pole
9.1.4.1 | 630/800 A Rating ,50 kA | Each | 181726 | 16226
9.1.4.2 | 1000 A Rating , 50 kA | Each | 188157 | 16800
9.1.4.3 | 1250 A Rating ,50 kA | Each | 200901 | 17938
9.1.4.4 | 1600 A Rating ,50 kA | Each | 226608 | 20233
9.1.4.5 | 2000 A Rating ,50 kA | Each | 268520 | 23975
9.1.4.6 | 2500 A Rating ,50 kA | Each | 319528 | 28529
9.1.4.7 | 3200 A Rating ,65 kA | Each | 387850 | 34525
9.1.4.8 | 4000 A Rating ,65 kA | Each | 251085 | 46525
9.2 | Supply and fixing of following accessories for Air circuit breaker (ACB) in existing ACB including making connection etc complete in all respect.
9.2.1 | Mechanical Interlocking Kit using key & Lock | Each | 8996 | 803
9.2.2 | Closing Release | Each | 11177 | 998
9.2.3 | Shunt Trip Release | Each | 2755 | 246
9.2.4 | Under voltage Release | Each | 3831 | 342
9.2.5 | External Neutral CT cast resin | Each | 6177 | 552
9.2.6 | Microswitch for Indication | Each | 2204 | 197
9.2.7 | Operation Counter | Each | 7309 | 653
9.2.8 | Door Interlock | Each | 2924 | 261
9.2.9 | Auxiliary Contact 4 NO + 4 NC | Each | 4724 | 422
9.3 | SITC of 3 /4 pole current limiting Moulded case circuit breaker (MCCB) made of flame retardent & heat resistant material having following current rating, short circuit breaking capacity at 440/415 V, 50 Hz; O/L & S/C settings , conforming to IS/IEC 60947 P -2 :2003 with front face and centralised adjustable, trip free mechanisum, true contact position indicator, designed for both horizontal & vertical mounting without any adverse effect on electrical performance, suitable for operation from 50 to 55 degree and without derating upto 40 degree, pollution degree 3, having positive isolation capability, push (test) to trip, trip time less then 10 ms under s/c condition, Breaking capacity Ics = 100% Icu. U imp =8 KV, rated insulation voltage 690V. provision for UVR , shunt trip , earth fault trip, door interlock, pad lock & rotary handle ( to be paid extra) , including making connections etc. as required. OEM shall have submit NABL / CPRI / ERDA/ Intertek accrediated lab type test certificate.
9.3.1 | 3 pole MCCB With Thermal Magnetic release
9.3.1.1 | up to 100 Amp , 10 kA, fixed O/L & fixed S/C setting | Each | 1506 | 135
9.3.1.2 | up to 100 Amp , 25 kA, adjustable O/L & Fixed S/C setting, | Each | 4506 | 402
9.3.1.3 | 125 Amp , 25 kA, adjustable O/L & fixed S/C setting, | Each | 5483 | 490
9.3.1.4 | 160 Amp , 25 kA, adjustable O/L & fixed S/C setting, | Each | 8821 | 788
9.3.1.5 | 200 Amp , 25 kA, adjustable O/L & fixed S/C setting, | Each | 11461 | 1023
9.3.1.6 | 250 Amp , 25 kA, adjustable O/L & adjustable S/C setting, | Each | 13403 | 1197
9.3.1.7 | 250 Amp , 35 kA, adjustable O/L & adjustable S/C setting, | Each | 13961 | 1247
9.3.1.8 | 400 Amp , 35 kA, adjustable O/L & adjustable S/C setting, | Each | 17134 | 1530
9.3.1.9 | 630 Amp , 50 kA, adjustable O/L & adjustable S/C setting, | Each | 24115 | 2153
9.3.1.10 | 800 Amp , 50 kA, adjustable O/L & adjustable S/C setting, | Each | 29446 | 2629
9.3.2 | 3 pole MCCB With Microprocessor based release with adjustable O/L & S/C setting with Inbuilt Instantaneous and Ground fault Protection.
9.3.2.1 | 250 Amp , 25 kA | Each | 26273 | 2346
9.3.2.2 | 400 Amp , 35 kA | Each | 30461 | 2720
9.3.2.3 | 630 Amp , 50 kA | Each | 32999 | 2946
9.3.2.4 | 800 Amp , 50 kA | Each | 56556 | 5050
9.3.3 | 4 pole MCCB With Thermal Magnetic release
9.3.3.1 | up to 100 Amp , 10 kA, fixed O/L & fixed S/C setting | Each | 1932 | 173
9.3.3.2 | up to 100 Amp , 25 kA, adjustable O/L & Fixed S/C setting, | Each | 6219 | 555
9.3.3.3 | 125 Amp , 25 kA, adjustable O/L & Fixed S/C setting, | Each | 7234 | 646
9.3.3.4 | 160 Amp , 25 kA, adjustable O/L & Fixed S/C setting, | Each | 10466 | 935
9.3.3.5 | 200 Amp , 25 kA, adjustable O/L & Fixed S/C setting, | Each | 13403 | 1197
9.3.3.6 | 250 Amp , 25 kA, adjustable O/L & adjustable S/C setting, | Each | 15243 | 1361
9.3.3.7 | 250 Amp , 35 kA, adjustable O/L & adjustable S/C setting, | Each | 17464 | 1559
9.3.3.8 | 400 Amp , 35 kA, adjustable O/L & adjustable S/C setting, | Each | 20942 | 1870
9.3.3.9 | 630 Amp , 50 kA, adjustable O/L & adjustable S/C setting, | Each | 29446 | 2629
9.3.3.10 | 800 Amp , 50 kA, adjustable O/L & adjustable S/C setting, | Each | 33126 | 2958
9.3.4 | 4 pole MCCB With Microprocessor based release with adjustable O/L & S/C setting with Inbuilt Instantaneous and Ground fault Protection.
9.3.4.1 | Upto 160 Amp , 50 kA | Each | 32710 | 2921
9.3.4.2 | 250 Amp , 50 kA | Each | 35689 | 3187
9.3.4.3 | 400 Amp , 50 kA | Each | 38274 | 3417
9.3.4.4 | 630 Amp, 50 kA | Each | 42585 | 3802
9.3.4.5 | 800 Amp , 50 kA | Each | 70478 | 6293
9.4 | Supply and fixing of following accessories for Moulded case circuit breaker (MCCB) compatible to main MCCB OEM as per PWD specification for electrical Works, conforming to IS/IEC 60947 P - 2 :2003 including making connection etc complete in all respect.
9.4.1 | Shunt Trip Release | Each | 12261 | 113
9.4.2 | Under Voltage Release | Each | 2481 | 222
9.4.3 | Extended Rotary Handle | Each | 2324 | 208
9.4.4 | Direct Rotary Handle | Each | 1352 | 121
9.4.5 | Mechanical Interlocking kit | Each | 6130 | 547
9.4.6 | Motor mechanism for 250A MCCB (240V, 50Hz) | Each | 19819 | 1770
9.4.7 | Motor mechanism for 400A MCCB (240V, 50Hz) | Each | 24855 | 2219
9.4.8 | Motor mechanism for 630A MCCB (240V, 50Hz) | Each | 38312 | 3421
9.4.9 | Auxiliary contact | Each | 1183 | 106
9.4.10 | Trip Alarm contact | Each | 1183 | 106
9.4.11 | Auxiliary + Trip alarm contact | Each | 1400 | 125
9.4.12 | Spreaders upto 125A, 3 Pole MCCB | Set | 315 | 28.1039
9.4.13 | Spreaders for 160A, 3 Pole MCCB | Set | 1070 | 95.5
9.4.14 | Spreaders for 160A, 4 Pole MCCB | Set | 1408 | 126
9.4.15 | Spreaders for 250A, 3 Pole MCCB | Set | 1070 | 95.5
9.4.16 | Spreaders for 250A, 4 Pole MCCB | Set | 1408 | 126
9.4.17 | Spreaders for 400A, 3Pole MCCB | Set | 2023 | 181
9.4.18 | Spreaders for 400A, 4Pole MCCB | Set | 2899 | 259
9.4.19 | Spreaders for 630A, 3Pole MCCB | Set | 2338 | 209
9.4.20 | Spreaders for 630A, 4Pole MCCB | Set | 3151 | 281
9.4.21 | Spreaders for 800A, 3Pole MCCB | Set | 4926 | 440
9.4.22 | Spreaders for 800A, 4Pole MCCB | Set | 6285 | 561
9.4.23 | Phase Barriers up to 630A, 3/4Pole MCCB | Set | 1206 | 108
9.4.24 | External Neutral CT with Adaptor Kit | Set | 4229 | 378
9.4.25 | Current Metering Module | Set | 18032 | 1610
9.5 | Providing & Fixing of IK08 and IP-30 Recessed/surface mounting heavy duty Enclosure suitable for mounting 3 / 4 pole MCCB, Inbuilt neutral linkmade out from Galvanized steel / CRCA sheet not less then 1.2 mm thick conforming to IS-8623-1 & 3 / IEC 61439- 1 & 3. powder painted complete with din rail making internal DB terminations, detachable gland plate, including making connections, testing etc. as required.
9.5.1 | Suitable to accommodate up to 70 sqmm 3.5 core Al arm. Cable | Each | 1800 | 161
9.5.2 | Suitable to accommodate above 70 sqmm 3.5 core Al arm. Cable to 185 Sqm , 3.5 core Al Arm. Cable | Each | 3825 | 342
9.6 | SITC of IP-43 surface mounting heavy duty modular Sub main Distribution board (SMDB) fabricated by MCCB OEM in his own factory having short circuit withstand current 35 kA (upto 400 amp.Incomer ) and 50 kA for 630 amp. Incomer with suitable bottom cabling box, 4 no. corner boxes, 2 no. side cabling boxes, metering Extension box with provision of incomer suitable for 3/4 pole MCCB and 3/4 pole MCCB as outgoing, Ammeter, Voltmeter, Indicating lamp, made out from Galvanized steel / CRCA sheet of 1.2/1.6 mm thick conforming to IEC 61439 Part 1 & 2. , U imp 8 KV, form of separation 2b, powder painted complete with insulated suitable rating tinned copper bus bar, neutral bars with shrouds, earth bar , din bar, making internal DB terminations with copper lugs, detachable gland plate, including making connections, testing etc. as required. (Without MCCB, ammeter, voltmeter, selector switch , Indicating lamp)
9.6.1 | SMDB with 250 Amp. Incoming and 4 no. 100 Amps Outgoing | Set | 57413 | 2683
9.6.2 | SMDB with 250 Amp. Incoming and 8 no. 100 Amps Outgoing | Set | 66581 | 3111
9.6.3 | SMDB with 250 Amp. Incoming and 12 no. 100 Amps Outgoing | Set | 73232 | 3422
9.6.4 | SMDB with 400 Amp. Incoming and 4 no. 100 Amps Outgoing | Set | 61009 | 2851
9.6.5 | SMDB with 400 Amp. Incoming and 8 no. 100 Amps Outgoing | Set | 65675 | 3069
9.6.6 | SMDB with 400 Amp. Incoming and 12 no. 100 Amps Outgoing | Set | 76567 | 3578
9.6.7 | SMDB with 630 Amp. Incoming and 4 no. 100 Amps Outgoing | Set | 87421 | 4085
9.6.8 | SMDB with 630 Amp. Incoming and 8 no. 100 Amps Outgoing | Set | 90279 | 4219
9.6.9 | SMDB with 630 Amp. Incoming and 12 no. 100 Amps Outgoing | Set | 112267 | 5246
9.6.10 | SMDB with 630 Amp. Incoming and 6 no. 100 Amps + 2 No. 250 amp. Outgoing | Set | 92717 | 4333
9.6.11 | SMDB with 630 Amp. Incoming and 10 no. 100 Amps + 2 No. 250 amp. Outgoing | Set | 113891 | 5322
Note:
1 | Neutral of Four pole MCCB should be protected against O/L & S/C protection.
2 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## ch 10 SFU & Changeovers
Chapter E - 10
Switch Fuse Unit & Change over switch
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
10.1 | Providing & Fixing of TP&N 415 V side handle operated double break fuse switch unit in sheet steel enclosure confirming to IS/lEC 60947-3 : 1999 (W/O HBC fuses) including making connections with suitable lugs, testing etc. as required.
10.1.1 | 63 A rating | Each | 6198 | 553
10.1.2 | 100 A rating | Each | 8377 | 748
10.1.3 | 200 A rating | Each | 14274 | 1274
10.1.4 | 300/320 A rating | Each | 16078 | 1436
10.1.5 | 400 A rating | Each | 23069 | 2060
10.1.6 | 500 A rating | Each | 32601 | 2911
10.2 | Providing & Fixing of TP&N 415 V AC-23A front handle operated switch disconnector fuse unit, cubical type, with metallic enclosure confirming to IS/lEC 60947-3 : 1999 with HBC fuses including making connections with lugs, testing etc as required.
10.2.1 | 32 A rating | Each | 3492 | 312
10.2.2 | 63 A rating | Each | 4172 | 373
10.2.3 | 100/125 A rating | Each | 6784 | 606
10.2.4 | 160 A rating | Each | 8583 | 766
10.2.5 | 200 A rating | Each | 11761 | 1050
10.2.6 | 250 A rating | Each | 13280 | 1186
10.2.7 | 300/320 A rating | Each | 15340 | 1370
10.2.8 | 400 A rating | Each | 17425 | 2516
10.2.9 | 630 A rating | Each | 28179 | 2516
10.3 | Providing & Fixing of TP&N 415 V AC-23A front handle operated switch disconnector fuse unit, cubical type, without metallic enclosure (For Panel Mounting) conforming to IS/lEC 60947-3 : 1999 in existing panel With HBC fuses including making connections with lugs, testing etc as required.
10.3.1 | 32 A rating | Each | 1533 | 137
10.3.2 | 63 A rating | Each | 2132 | 190
10.3.3 | 100/125 A rating | Each | 4697 | 419
10.3.4 | 160 A rating | Each | 6651 | 594
10.3.5 | 200 A rating | Each | 8443 | 754
10.3.6 | 250 A rating | Each | 9868 | 881
10.3.7 | 300/320 A rating | Each | 12174 | 1087
10.3.8 | 400 A rating | Each | 14639 | 1307
10.3.9 | 630 A rating | Each | 23455 | 2094
10.4 | Providing & Fixing of bolted type/ Din type HBC (High breaking capacity) fuse links of 80 KA breaking capacity confirming to IS:13703 in the existing fuse base, fuse switch unit etc. of the following type and rating.
10.4.1 | Cylindrical Fuse Link
10.4.1.1 | 2 A to 32 A | Each | 82.5 | 7
10.4.1.2 | 40 A | Each | 92.7 | 8
10.4.1.3 | 50 A | Each | 197 | 18
10.4.1.4 | 63A | Each | 235 | 21
10.4.2 | Offset tag type
10.4.2.1 | 2 A to 20 A | Each | 40.6 | 4
10.4.2.2 | 25 A to 32 A | Each | 69.8 | 6
10.4.2.3 | 35 A to 63 A | Each | 95.2 | 8
10.4.2.4 | 80 A to 125 A | Each | 317 | 28
10.4.3 | Central tag type
10.4.3.1 | 80 A to 125 A | Each | 260 | 23
10.4.3.2 | 160 A to 200 A | Each | 298 | 27
10.4.3.3 | 250 A to 315 A | Each | 438 | 39
10.4.3.4 | 400 A to 500 A | Each | 1307 | 117
10.4.3.5 | 630 A | Each | 1422 | 127
10.4.4 | Din (knife type) type
10.4.4.1 | 63 A to 125 A Size 000 | Each | 324 | 29
10.4.4.2 | 63 A to 160 A Size 00 | Each | 350 | 31
10.4.4.3 | 80 A to 200 A Size 0 | Each | 463 | 41
10.4.4.4 | 125 A to 315 A Size 1 | Each | 578 | 52
10.4.4.5 | 200 A to 400 A Size 2 | Each | 819 | 73
10.4.4.6 | 315A to 800 A Size 3 | Each | 2373 | 212
10.5 | Providing & Fixing of on load change over switch, front handle operated, four pole 415 V confirming to IS/lEC 60947-3 : 1999 including connections , testing etc. as required .in the following rating.
10.5.1 | Open execution type
10.5.1.1 | 63 A | Each | 3440 | 307
10.5.1.2 | 125 A | Each | 6473 | 307
10.5.1.3 | 160 A | Each | 8250 | 737
10.5.1.4 | 200 A | Each | 10560 | 943
10.5.1.5 | 250 A | Each | 15231 | 1360
10.5.1.6 | 320 A | Each | 16754 | 1496
10.5.1.7 | 400 A | Each | 24559 | 2193
10.5.1.8 | 630 A | Each | 30715 | 2742
10.5.1.9 | 800 A | Each | 41884 | 3740
10.5.1.10 | 1000 A | Each | 45945 | 4102
10.5.2 | With OEM fabricated sheet steel enclosure, powder coated, door locking system allow opening of door in OFF position only with 2 nos external earthing points.
10.5.2.1 | 63 A | Each | 5394 | 482
10.5.2.2 | 125 A | Each | 9352 | 835
10.5.2.3 | 160 A | Each | 11622 | 1038
10.5.2.4 | 200 A | Each | 13542 | 1209
10.5.2.5 | 250 A | Each | 18086 | 1615
10.5.2.6 | 320 A | Each | 21888 | 1954
10.5.2.7 | 400 A | Each | 30353 | 2710
10.5.2.8 | 630 A | Each | 36426 | 3252
10.5.2.9 | 800 A | Each | 53027 | 4735
10.5.2.10 | 1000 A | Each | 63162 | 5640
10.6 | Providing & Fixing of off load change over switch four pole/two pole, 230/ 415 V ,side handle operated confirming to IS:13947 P-III in sheet steel enclosure complete with connections with lugs, testing etc. as required in the following rating:
10.6.1 | 32 A, Double pole | Each | 1498 | 134
10.6.2 | 32 A, Four pole | Each | 2513 | 224
10.6.3 | 63 A Four pole | Each | 4633 | 414
10.6.4 | 100 A Four pole | Each | 9075 | 810
10.6.5 | 200 A Four pole | Each | 14095 | 1258
10.6.6 | 315 A Four pole | Each | 17967 | 1604
10.6.7 | 400 A Four pole | Each | 20584 | 1838
10.7 | Providing & Fixing of Four Pole By pass Change Over Switch confirming to IS:13947(Part 3) : IEC:60947-3-1 and IEC:60947-6-1, Open execution type in the following ratings.
10.7.1 | 63 A | Each | 12467 | 1113
10.7.2 | 100 A | Each | 14120 | 1261
10.7.3 | 200 A | Each | 19510 | 1742
10.7.4 | 320 A | Each | 29439 | 2629
10.7.5 | 400 A | Each | 44165 | 3943
10.7.6 | 630 A | Each | 50176 | 4480
10.7.7 | 800 A | Each | 64401 | 5750
10.7.8 | 1000 A | Each | 116362 | 10390
10.8 | Providing & Fixing of bus bar chamber housed in sheet metal box Confirming to IEC-60439/IS-8623 & IEC-60529/IS-2147 made out from 1.6 mm thick powder coated CRCA sheet,degree of protection IP-31, front openable bus bar made out of aluminium or wrought aluminium alloy suitable for 100 amp. Capacity , bus bar fixed on porcelain/DMC insulators at approved spacing including making connections etc. as required.
10.8.1 | 300 mm long , 2 strip | Each | 869 | 78
10.8.2 | 300 mm long , 4 strip | Each | 1066 | 95
10.8.3 | 450 mm long , 2 strip | Each | 1333 | 119
10.8.4 | 450 mm long , 4 strip | Each | 1800 | 161
10.8.5 | 600 mm long ,2 strip | Each | 1682 | 150
10.8.6 | 600 mm long , 4 strip | Each | 1955 | 175
10.8.7 | 900 mm long , 2 strip | Each | 2399 | 214
10.8.8 | 900 mm long , 4 strip | Each | 2776 | 248
10.9 | Providing & Fixing of bus bar chamber housed in sheet metal box Confirming to IEC-60439/ IS-8623 & IEC-60529/ IS-2147 made out from 1.6 mm thick powder coated CRCA sheet,degree of protection IP-31 front openable bus bar made out of aluminium or wrought aluminium alloy suitable for 200 amp. Capacity , bus bar fixed on porcelain/DMC insulators at approved spacing including making connections etc. as required.
10.9.1 | 300 mm long , 4 strip | Each | 1466 | 131
10.9.2 | 450 mm long , 4 strip | Each | 2333 | 208
10.9.3 | 600 mm long , 4 strip | Each | 2499 | 223
10.9.4 | 900 mm long , 4 strip | Each | 3399 | 304
10.10 | Providing & Fixing of bus bar chamber housed in sheet metal box Confirming to IEC-60439/IS-8623 & IEC-60529/IS-2147 made out from 1.6 mm thick powder coated CRCA sheet,degree of protection IP-31, front openable bus bar made out of Copper suitable for 100 amp. Capacity , bus bar fixed on porcelain/DMC insulators at approved spacing including making connections etc. as required.
10.10.1 | 300 mm long , 2 strip | Each | 1866 | 167
10.10.2 | 300 mm long , 4 strip | Each | 3998 | 357
10.10.3 | 450 mm long , 2 strip | Each | 2266 | 202
10.10.4 | 450 mm long , 4 strip | Each | 4664 | 417
10.10.5 | 600 mm long ,2 strip | Each | 3065 | 274
10.10.6 | 600 mm long , 4 strip | Each | 6130 | 547
10.10.7 | 900 mm long , 2 strip | Each | 4265 | 381
10.10.8 | 900 mm long , 4 strip | Each | 7996 | 714
10.11 | Providing & Fixing of bus bar chamber housed in sheet metal box Confirming to IEC-60439/IS-8623 & IEC-60529/IS-2147 made out from 1.6 mm thick powder coated CRCA sheet,degree of protection IP-31, front openable bus bar made out of Copper suitable for 200 amp. Capacity , bus bar fixed on porcelain/DMC insulators at approved spacing including making connections etc. as required.
10.11.1 | 300 mm long , 4 strip | Each | 4664 | 417
10.11.2 | 450 mm long , 4 strip | Each | 5331 | 476
10.11.3 | 600 mm long , 4 strip | Each | 7730 | 690
10.11.4 | 900 mm long , 4 strip | Each | 10661 | 952

## Ch 11 LT cables
Chapter E - 11
LT Cables
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
11.1 | Providing & Laying XLPE insulated & P.V.C. sheathed Un-Armoured Aluminium cable confirming to IS :7098 P - I of 1.1 KV with H4- Grade electrolytic aluminium conductor confirming to IS 8130 of purity >99.6 %, sheath confirming to IS:5831 in existing RCC / Hume / Stoneware / PVC pipe/ open duct/cable trench / Cable tray (with cable tie) including testing commissioning etc. as required of following size.
11.1.1 | 4.0 Sq. mm
11.1.1.1 | 2 core | Mtr | 54 | 6
11.1.1.2 | 3 core | Mtr | 67 | 6
11.1.1.3 | 4 core | Mtr | 80 | 6
11.1.2 | 6.0 Sq. mm
11.1.2.1 | 2 core | Mtr | 74 | 6
11.1.2.2 | 3 core | Mtr | 87 | 6
11.1.2.3 | 4 core | Mtr | 106 | 8
11.1.3 | 10.0 Sq. mm
11.1.3.1 | 2 core | Mtr | 104 | 6
11.1.3.2 | 3 core | Mtr | 115 | 6
11.1.3.3 | 4 core | Mtr | 138 | 9
11.1.4. | 16.0 Sq. mm
11.1.4.1 | 2 core | Mtr | 106 | 7
11.1.4.2 | 3 core | Mtr | 130 | 7
11.1.4.3 | 4 core | Mtr | 175 | 11
11.1.5 | 25.0 Sq. mm
11.1.5.1 | 2 core | Mtr | 138 | 9
11.1.5.2 | 3 core | Mtr | 190 | 9
11.1.5.3 | 3.5 core | Mtr | 243 | 13
11.1.6 | 35.0 Sq. mm
11.1.6.1 | 2 core | Mtr | 180 | 11
11.1.6.2 | 3 core | Mtr | 252 | 11
11.1.6.3 | 3.5 core | Mtr | 277 | 17
11.1.7 | 50.0 Sq. mm
11.1.7.1 | 2 core | Mtr | 226 | 13
11.1.7.2 | 3 core | Mtr | 309 | 13
11.1.7.3 | 3.5 core | Mtr | 371 | 20
11.1.8 | 70.0 Sq. mm
11.1.8.1 | 2 core | Mtr | 323 | 17
11.1.8.2 | 3 core | Mtr | 442 | 17
11.1.8.3 | 3.5 core | Mtr | 503 | 22
11.1.9 | 95.0 Sq. mm
11.1.9.1 | 1 core | Mtr | 203 | 22
11.1.9.2 | 3.5 core | Mtr | 572 | 28
11.1.10 | 120.0 Sq. mm
11.1.10.1 | 1 core | Mtr | 252 | 28
11.1.10.2 | 3.5 core | Mtr | 738 | 39
11.1.11 | 150.0 Sq. mm
11.1.11.1 | 1 core | Mtr | 311 | 33
11.1.11.2 | 3.5 core | Mtr | 863 | 44
11.1.12 | 185.0 Sq. mm
11.1.12.1 | 1 core | Mtr | 388 | 44
11.1.12.2 | 3.5 core | Mtr | 1113 | 67
11.1.13 | 240.0 Sq. mm
11.1.13.1 | 1 core | Mtr | 491 | 56
11.1.13.2 | 3.5 core | Mtr | 1358 | 78
11.1.14 | 300.0 Sq. mm
11.1.14.1 | 1 core | Mtr | 604 | 67
11.1.14.2 | 3.5 core | Mtr | 1749 | 89
11.1.15 | 400.0 Sq. mm
11.1.15.1 | 1 core | Mtr | 770 | 111
11.1.15.2 | 3.5 core | Mtr | 2184 | 111
11.1.16 | 500.0 Sq. mm
11.1.16.1 | 1 core | Mtr | 959 | 89
11.1.16.2 | 3.5 core | Mtr | 2994 | 133
11.2 | Providing & Laying XLPE insulated & P.V.C. sheathed Armoured Aluminium cable confirming to IS :7098 P - I of 1.1 KV with H4- Grade electrolytic aluminium conductor confirming to IS 8130 of purity >99.6 %, round / flat strip armouring of cables, Inner / outer sheath confirming to IS:5831 in existing RCC / Hume / Stoneware / PVC pipe/ open duct/cable trench / Cable tray(with cable tie) including testing commissioning etc. as required of following size.
11.2.1 | 4.0 Sq. mm
11.2.1.1 | 2 core | Mtr | 95 | 8
11.2.1.2 | 3 core | Mtr | 101 | 8
11.2.1.3 | 4 core | Mtr | 118 | 9
11.2.2 | 6.0 Sq. mm
11.2.2.1 | 2 core | Mtr | 113 | 8
11.2.2.2 | 3 core | Mtr | 123 | 8
11.2.2.3 | 4 core | Mtr | 146 | 9
11.2.3 | 10.0 Sq. mm
11.2.3.1 | 2 core | Mtr | 143 | 9
11.2.3.2 | 3 core | Mtr | 157.9971 | 9
11.2.3.3 | 4 core | Mtr | 179 | 11
11.2.4 | 16.0 Sq. mm
11.2.4.1 | 2 core | Mtr | 160 | 9
11.2.4.2 | 3 core | Mtr | 172 | 11
11.2.4.3 | 4 core | Mtr | 217 | 14
11.2.5 | 25.0 Sq. mm
11.2.5.1 | 2 core | Mtr | 173 | 11
11.2.5.2 | 3 core | Mtr | 226 | 13
11.2.5.3 | 3.5 core | Mtr | 264 | 17
11.2.6 | 35.0 Sq. mm
11.2.6.1 | 2 core | Mtr | 216 | 13
11.2.6.2 | 3 core | Mtr | 287 | 17
11.2.6.3 | 3.5 core | Mtr | 323 | 22
11.2.7 | 50.0 Sq. mm
11.2.7.1 | 2 core | Mtr | 279 | 17
11.2.7.2 | 3 core | Mtr | 371 | 19.998
11.2.7.3 | 3.5 core | Mtr | 435 | 28
11.2.8 | 70.0 Sq. mm
11.2.8.1 | 1 core | Mtr | 235 | 19.998
11.2.8.2 | 2 core | Mtr | 373 | 22
11.2.8.3 | 3 core | Mtr | 510 | 28
11.2.8.4 | 3.5 core | Mtr | 581 | 33
11.2.9 | 95.0 Sq. mm
11.2.9.1 | 1 core | Mtr | 252 | 22
11.2.9.2 | 3.5 core | Mtr | 652 | 44
11.2.10 | 120.0 Sq. mm
11.2.10.1 | 1 core | Mtr | 294 | 44
11.2.10.2 | 3.5 core | Mtr | 817 | 39
11.2.11 | 150.0 Sq. mm
11.2.11.1 | 1 core | Mtr | 350 | 33
11.2.11.2 | 3.5 core | Mtr | 958 | 56
11.2.12 | 185.0 Sq. mm
11.2.12.1 | 1 core | Mtr | 434 | 44
11.2.12.2 | 3.5 core | Mtr | 1214 | 72
11.2.13 | 240.0 Sq. mm
11.2.13.1 | 1 core | Mtr | 536 | 56
11.2.13.2 | 3.5 core | Mtr | 1523 | 89
11.2.14 | 300.0 Sq. mm
11.2.14.1 | 1 core | Mtr | 659 | 67
11.2.14.2 | 3.5 core | Mtr | 1859 | 94
11.2.15 | 400.0 Sq. mm
11.2.15.1 | 1 core | Mtr | 826 | 78
11.2.15.2 | 3.5 core | Mtr | 2372 | 117
11.2.16 | 500.0 Sq. mm
11.2.16.1 | 1 core | Mtr | 1021 | 89
11.2.16.2 | 3.5 core | Mtr | 3337 | 150
11.3 | Providing & Laying XLPE insulated & P.V.C. sheathed Un-armoured Copper cable confirming to IS :7098 P - I of 1.1 KV with electrolytic grade Copper made of copper rods confirming to IS 613-1964, of purity >99.7 %, sheath confirming to IS:5831 in existing RCC / Hume / Stoneware / PVC pipe/ open duct/cable trench / Cable tray (with cable tie) including testing commissioning etc. as required of following size.
11.3.1 | 1.5 Sq. mm
11.3.1.1 | 2 core | Mtr | 71 | 6
11.3.1.2 | 3 core | Mtr | 99 | 6
11.3.1.3 | 4 core | Mtr | 126 | 6
11.3.1.4 | 6 core | Mtr | 171 | 8
11.3.1.5 | 8 core | Mtr | 232 | 8
11.3.1.6 | 10 core | Mtr | 278 | 11
11.3.1.7 | 12 core | Mtr | 299 | 13
11.3.2 | 2.5 Sq. mm
11.3.2.1 | 2 core | Mtr | 106 | 6
11.3.2.2 | 3 core | Mtr | 145 | 6
11.3.2.3 | 4 core | Mtr | 194 | 6
11.3.2.4 | 6 core | Mtr | 288 | 8
11.3.2.5 | 8 core | Mtr | 368 | 8
11.3.2.6 | 10 core | Mtr | 425 | 11
11.3.2.7 | 12 core | Mtr | 520 | 13
11.3.3 | 4.0 Sq. mm
11.3.3.1 | 2 core | Mtr | 144 | 6
11.3.3.2 | 3 core | Mtr | 203 | 6
11.3.3.3 | 4 core | Mtr | 252 | 8
11.3.4 | 6.0 Sq. mm
11.3.4.1 | 2 core | Mtr | 208 | 6
11.3.4.2 | 3 core | Mtr | 297 | 6
11.3.4.3 | 4 core | Mtr | 369 | 11
11.3.5 | 10.0 Sq. mm
11.3.5.1 | 2 core | Mtr | 358 | 8
11.3.5.2 | 3 core | Mtr | 501 | 8
11.3.5.3 | 4 core | Mtr | 544 | 13
11.3.6 | 16.0 Sq. mm
11.3.6.1 | 1 core | Mtr | 267 | 8
11.3.6.2 | 2 core | Mtr | 501 | 8
11.3.6.3 | 3 core | Mtr | 724 | 9
11.3.6.4 | 4 core | Mtr | 912 | 13
11.3.7 | 25.0 Sq. mm
11.3.7.1 | 1 core | Mtr | 425 | 9
11.3.7.2 | 2 core | Mtr | 830 | 9
11.3.7.3 | 3 core | Mtr | 1151 | 9.999
11.3.7.4 | 4 core | Mtr | 1508 | 13
11.4 | Providing & Laying XLPE insulated & P.V.C. sheathed Armoured Copper cable confirming to IS :7098 P - I of 1.1 KV with electrolytic grade Copper made of copper rods confirming to IS 613-1964, of purity >99.7 %, round / flat strip armouring, Inner / outer sheath confirming to IS:5831 in existing RCC / Hume / Stoneware / PVC pipe/ open duct/cable trench / Cable tray(with cable tie) including testing etc. as required of following size.
11.4.1 | 1.5 Sq. mm
11.4.1.1 | 2 core | Mtr | 85.5 | 7
11.4.1.2 | 3 core | Mtr | 110 | 7
11.4.1.3 | 4 core | Mtr | 135 | 7
11.4.1.4 | 6 core | Mtr | 196 | 9
11.4.1.5 | 8 core | Mtr | 254 | 9
11.4.1.6 | 10 core | Mtr | 290 | 13
11.4.1.7 | 12 core | Mtr | 321 | 16
11.4.2 | 2.5 Sq. mm
11.4.2.1 | 2 core | Mtr | 127 | 7
11.4.2.2 | 3 core | Mtr | 160 | 7
11.4.2.3 | 4 core | Mtr | 206 | 7
11.4.2.4 | 6 core | Mtr | 297 | 9
11.4.2.5 | 8 core | Mtr | 375 | 9
11.4.2.6 | 10 core | Mtr | 435 | 13
11.4.2.7 | 12 core | Mtr | 506 | 16
11.4.3 | 4.0 Sq. mm
11.4.3.1 | 2 core | Mtr | 158 | 8
11.4.3.2 | 3 core | Mtr | 209 | 8
11.4.3.3 | 4 core | Mtr | 267 | 9.999
11.4.4 | 6.0 Sq. mm
11.4.4.1 | 2 core | Mtr | 219 | 8
11.4.4.2 | 3 core | Mtr | 298 | 8
11.4.4.3 | 4 core | Mtr | 392 | 13
11.4.5 | 10.0 Sq. mm
11.4.5.1 | 2 core | Mtr | 345 | 9
11.4.5.2 | 3 core | Mtr | 480 | 9
11.4.5.3 | 4 core | Mtr | 619 | 17
11.4.6 | 16.0 Sq. mm
11.4.6.1 | 1 core | Mtr | 298 | 11
11.4.6.2 | 2 core | Mtr | 509 | 11
11.4.6.3 | 3 core | Mtr | 702 | 12
11.4.6.4 | 4 core | Mtr | 906 | 14
11.4.7 | 25.0 Sq. mm
11.4.7.1 | 1 core | Mtr | 436 | 12
11.4.7.2 | 2 core | Mtr | 802 | 12
11.4.7.3 | 3 core | Mtr | 1131 | 14
11.4.7.4 | 4 core | Mtr | 1489 | 17
11.4.8 | 35 Sq. mm
11.4.8.1 | 1 core | Mtr | 589 | 13
11.4.8.2 | 2 core | Mtr | 1138 | 17
11.4.8.3 | 3 core | Mtr | 1592 | 19
11.4.8.4 | 4 core | Mtr | 2111 | 22
11.4.9 | 50 Sq. mm
11.4.9.1 | 1 core | Mtr | 796 | 17
11.4.9.2 | 2 core | Mtr | 1485 | 20
11.4.9.3 | 3 core | Mtr | 2149 | 22
11.4.9.4 | 4 core | Mtr | 2861 | 28
11.5 | Excavation of trench of size 75 cm (Depth) x 35 cm(Width) for laying of suitable no. of LT cables (Inter spacing between cables should not be less than 2 D) in ground with following procedure :- (a) Make a river sand bed of height 100 mm along the trench, (b) Lay the cable in the middle of the trench, (c) Provide river sand bed of height 100 mm on top of the cable, (d) Lay the protective Common burnt clay F.P.S. Bricks of Class designation 75 / Sand stone slabs of 50 mm thickness and 225 mm wide just above the sand bed vertically across the cable, (e) Backfill the excavated soil leaving 300 mm from the Ground level, (f)Lay the Cable warning tape and again back-fill the remaining portion of the trench upto the ground level and compacting the earth. | Mtr | 145 | 61
11.6 | Add Extra in Item no.11.5 if Excavation done in Hard Rock / CC road / TAR Road and making Good the same | Mtr | 44 | 44
11.7 | Excavation of trench of size additional 20 cm in width, with procedure as per following points :- (a) Make a river sand bed of height 100 mm along the trench, (b) Lay another cable in middle of trench in such manner that spacing between another cable is 20 cm., (c) Provide river sand bed of height 100 mm on top of the cable. (d) Lay the protective Common burnt clay F.P.S. Bricks of Class designation 75 /Sand stone slabs of 50 mm thickness and 225 mm wide just above the sand bed vertically (Longest side is vertical to cable) along the cable , (e) Backfill the excavated soil leaving 300 mm from the Ground level, (f)Lay the Cable warning tape and again back-fill the remaining portion of the trench upto the ground level and compacting the earth | Mtr | 106 | 38
11.8 | Add Extra in Item no. 11.7 if Excavation done in Hard Rock / CC road / TAR Road and making Good the same | Mtr | 25 | 25
11.9 | Add Extra in item no. 11.1 to 11.4 for Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
11.9.1 | Up to 35 Sq.mm fixed with 25 mm x 2 mm thick suitable length red oxide and enamel painted MS clamp and base, pvc rawl plug and screws of sufficient size with spacing 0.6 Mtr. Between Clamps. | Mtr | 31 | 9
11.9.2 | Above 35 sq. mm and upto 95 sq. mm fixed with 40 mm x 3 mm thick suitable length red oxide and enamel painted MS clamp and base, pvc rawl plug and screws of sufficient size with spacing 0.6 Mtr. Between Clamps. | Mtr | 55 | 14
11.9.3 | Above 95 sq. mm and upto 185 sq. mm fixed with 40 mm x 4 mm thick suitable length red oxide and enamel painted MS clamp and base, pvc rawl plug and screws of sufficient size with spacing 0.6 Mtr. Between Clamps. | Mtr | 78 | 19
11.9.4 | Above 185 sq. mm and upto 400 sq. mm fixed with 50 mm x 5 mm thick suitable length red oxide and enamel painted MS clamp and base, pvc rawl plug and screws of sufficient size with spacing 0.6 Mtr. Between Clamps. | Mtr | 120 | 23
11.10. | Add extra in item no. 11.1 to 11.4 for Laying Charges for cable through Manual Boggi by making pit at regular interval and repairing the pit after laying of cable with PCC/ Bitumin as required. | Mtr | 133 | 133
11.11 | Add Extra in item no. 11.1 to 11.4 for Laying Charges for cable through Vermeer machine by making pit at regular interval and repairing the pit after laying of cable with PCC/ Bitumin as required. | Mtr | 333 | 333
Note:
1 | OEM must ensure that the cable is tested for compliance, through their in house laboratory accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and testing procedure as per IS:10810.
2 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 12 LT Cable Accessories
Chapter E - 12
LT Cable Accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
12.1 | Supplying and making one end termination with Nickel plated heavy duty brass single compression gland (as per IS 12943-1990)) SIBG type consisting of Check Nut, Gland Body, Metal Washer(3 Nos.), Outer Seal Rubber Ring, Compression Nut, heavy duty aluminium lugs (as per IS 8309 -1993) duly crimped with crimping tool, PVC tape as per IS 8337-1976 of following size of PVC insulated & PVC sheathed/ XLPE aluminium conductor cable of 1100 volt grade as required.
12.1.1 | 2 x 4.0 sq.mm | Set | 93 | 18
12.1.2 | 2 x 6.0 sq.mm | Set | 135 | 27
12.1.3 | 2 x 10.0 sq.mm | Set | 136 | 27
12.1.4 | 2 x 16.0 sq.mm | Set | 138 | 27
12.1.5 | 2 x 25.0 sq.mm | Set | 154 | 30
12.1.6 | 2 x 35.0 sq.mm | Set | 187 | 37
12.1.7 | 2 x 50.0 sq.mm | Set | 193 | 38
12.1.8 | 2 x 70.0 sq.mm | Set | 231 | 45
12.1.9 | 3 x 4.0 sq.mm | Set | 87 | 17
12.1.10 | 3 x 6.0 sq.mm | Set | 137 | 27
12.1.11 | 3 x 10.0 sq.mm | Set | 139 | 27
12.1.12 | 3 x 16.0 sq.mm | Set | 155 | 31
12.1.13 | 3 x 25.0 sq.mm | Set | 190 | 37
12.1.14 | 3 x 35.0 sq.mm | Set | 194 | 38
12.1.15 | 3 x 50.0 sq.mm | Set | 230 | 45
12.1.16 | 3 x 70.0 sq.mm | Set | 253 | 50
12.1.17 | 3.5 x 25.0 sq.mm | Set | 193 | 38
12.1.18 | 3.5 x 35.0 sq.mm | Set | 203 | 40
12.1.19 | 3.5 x 50.0 sq.mm | Set | 241 | 47
12.1.20 | 3.5 x 70.0 sq.mm | Set | 353 | 70
12.1.21 | 3.5 x 95.0 sq.mm | Set | 579 | 114
12.1.22 | 3.5 x 120.0 sq.mm | Set | 674 | 133
12.1.23 | 3.5 x 150.0 sq.mm | Set | 722 | 142
12.1.24 | 3.5 x 185.0 sq.mm | Set | 1037 | 204
12.1.25 | 3.5 x 240.0 sq.mm | Set | 1126 | 222
12.1.26 | 3.5 x 300.0 sq.mm | Set | 1407 | 277
12.1.27 | 3.5 x 400.0 sq.mm | Set | 2034 | 401
12.1.28 | 3.5 x 500.0 sq.mm | Set | 2634 | 516
12.1.29 | 3.5 x 630.0 sq.mm | Set | 3059 | 602
12.1.30 | 4 x 4.0 sq.mm | Set | 139 | 27
12.1.31 | 4 x 6.0 sq.mm | Set | 140 | 28
12.1.32 | 4 x 10.0 sq.mm | Set | 154 | 30
12.1.33 | 4 x 16.0 sq.mm | Set | 159 | 31
12.1.34 | 1 x 70.0 sq.mm | Set | 158 | 31
12.1.35 | 1 x 95.0 sq.mm | Set | 146 | 29
12.1.36 | 1 x 120.0 sq.mm | Set | 196 | 39
12.1.37 | 1 x 150.0 sq.mm | Set | 203 | 40
12.1.38 | 1 x 185.0 sq.mm | Set | 329 | 65
12.1.39 | 1 x 240.0 sq.mm | Set | 269 | 53
12.1.40 | 1 x 300.0 sq.mm | Set | 388 | 76
12.1.41 | 1 x 400.0 sq.mm | Set | 650 | 128
12.1.42 | 1 x 500.0 sq.mm | Set | 789 | 155
12.1.43 | 1 x 630.0 sq.mm | Set | 865 | 170
12.1.44 | 1 x 800.0 sq.mm | Set | 1584 | 312
12.1.45 | 1 x 1000.0 sq.mm | Set | 1765 | 348
12.2 | Supplying and making one end termination with Nickel plated heavy duty brass single compression gland (as per IS 12943-1990)) SIBG type consisting of Check Nut, Gland Body, Metal Washer(3 Nos.), Outer Seal Rubber Ring, Compression Nut, heavy duty Copper lugs (IS 8337- 1976) duly crimped with crimping tool, PVC tape for following size of PVC insulated & PVC sheathed/ XLPE copper conductor cable of 1100 volt grade as required.
12.2.1 | 1 x 16.0 sq.mm | Set | 100 | 20
12.2.2 | 1 x 25.0 sq.mm | Set | 125 | 25
12.2.3 | 1 x 35.0 sq.mm | Set | 132 | 26
12.2.4 | 1 x 50.0 sq.mm | Set | 174 | 34
12.2.5 | 1 x 70.0 sq.mm | Set | 204 | 40
12.2.6 | 1 x 95.0 sq.mm | Set | 248 | 49
12.2.7 | 1 x 120.0 sq.mm | Set | 317 | 62
12.2.8 | 2 x 4.0 sq.mm | Set | 119 | 23
12.2.9 | 2 x 6.0 sq.mm | Set | 122 | 23.9959
12.2.10 | 2 x 10.0 sq.mm | Set | 150 | 29
12.2.11 | 2 x 16.0 sq.mm | Set | 158 | 31
12.2.12 | 2 x 25.0 sq.mm | Set | 184 | 36
12.2.13 | 2 x 35.0 sq.mm | Set | 199 | 39
12.2.14 | 2 x 50.0 sq.mm | Set | 264 | 52
12.2.15 | 2 x 70.0 sq.mm | Set | 348 | 69
12.2.16 | 2 x 95.0 sq.mm | Set | 416 | 82
12.2.17 | 2 x 120.0 sq.mm | Set | 586 | 115
12.2.18 | 3 x 1.5 sq.mm | Set | 122 | 24
12.2.19 | 3 x 2.5 sq.mm | Set | 123 | 24
12.2.20 | 3 x 4.0 sq.mm | Set | 126 | 25
12.2.21 | 3 x 6.0 sq.mm | Set | 157 | 31
12.2.22 | 3 x 10.0 sq.mm | Set | 159 | 31
12.2.23 | 3 x 16.0 sq.mm | Set | 184 | 36
12.2.24 | 3 x 25.0 sq.mm | Set | 236 | 46
12.2.25 | 3 x 35.0 sq.mm | Set | 257 | 51
12.2.26 | 3 x 50.0 sq.mm | Set | 336 | 66
12.2.27 | 3 x 70.0 sq.mm | Set | 428 | 84
12.2.28 | 3 x 95.0 sq.mm | Set | 614 | 121
12.2.29 | 3 x 120.0 sq.mm | Set | 951 | 187
12.2.30 | 4 x 1.5 sq.mm | Set | 127 | 25
12.2.31 | 4 x 2.5 sq.mm | Set | 129 | 25
12.2.32 | 4 x 4.0 sq.mm | Set | 159 | 31
12.2.33 | 4 x 6.0 sq.mm | Set | 165 | 33
12.2.34 | 4 x 10.0 sq.mm | Set | 181 | 36
12.2.35 | 4 x 16.0 sq.mm | Set | 197 | 39
12.2.36 | 4 x 25.0 sq.mm | Set | 257 | 51
12.2.37 | 4 x 35.0 sq.mm | Set | 312 | 61
12.2.38 | 4 x 50.0 sq.mm | Set | 388 | 76
12.2.39 | 4 x 70.0 sq.mm | Set | 595 | 117
12.2.40 | 4 x 95.0 sq.mm | Set | 1014 | 200
12.2.41 | 4 x 120.0 sq.mm | Set | 1166 | 230
12.2.42 | 6 x 1.5 sq.mm | Set | 165 | 32
12.2.43 | 6 x 2.5 sq.mm | Set | 168 | 33
12.2.44 | 8 x 1.5 sq.mm | Set | 176 | 35
12.2.45 | 8 x 2.5 sq.mm | Set | 193 | 38
12.2.46 | 10 x 1.5 sq.mm | Set | 200 | 39
12.2.47 | 10 x 2.5 sq.mm | Set | 205 | 40
12.2.48 | 12 x 1.5 sq.mm | Set | 212 | 42
12.2.49 | 12 x 2.5 sq.mm | Set | 248 | 49
12.3 | Supplying and making end termination with heavy aluminium lugs ( Pin / ring type ) confirming to IS 8309 -1993 duly crimped with crimping tool, PVC tape etc of following size.
12.3.1 | 1.5 Sq.mm | Each | 2 | 0.5
12.3.2 | 2.5 Sq.mm | Each | 2 | 0.5
12.3.3 | 4.0 Sq.mm | Each | 2.5 | 0.5
12.3.4 | 6.0 Sq.mm | Each | 2.4 | 0.6
12.3.5 | 10.0 Sq.mm | Each | 2.8 | 0.5
12.3.6 | 16.0 Sq.mm | Each | 3.9 | 0.8
12.3.7 | 25.0 Sq.mm | Each | 5.4 | 1.1
12.3.8 | 35.0 Sq.mm | Each | 6.6 | 1.3
12.3.9 | 50.0 Sq.mm | Each | 9.5 | 1.9
12.3.10 | 70.0 Sq.mm | Each | 15 | 3
12.3.11 | 95.0 Sq.mm | Each | 16 | 3.1
12.3.12 | 120.0 Sq.mm | Each | 22 | 4.4
12.3.13 | 150.0 Sq.mm | Each | 29 | 5.8
12.3.14 | 185.0 Sq.mm | Each | 36 | 7.2
12.3.15 | 240.0 Sq.mm | Each | 62 | 12
12.3.16 | 300.0 Sq.mm | Each | 88 | 17
12.3.17 | 400.0 Sq.mm | Each | 127 | 25
12.3.18 | 500.0 Sq.mm | Each | 193 | 38
12.3.19 | 630.0 Sq.mm | Each | 245 | 48
12.3.20 | 800.0 Sq.mm | Each | 397 | 78
12.3.21 | 1000.0 Sq.mm | Each | 579 | 114
12.4 | Supplying and making end termination with heavy duty Copper lugs ( ANY type ) confirming to IS 8309 -1993 duly crimped with crimping tool, PVC tape etc of following size.
12.4.1 | 1.5 Sq.mm | Each | 5.7 | 1
12.4.2 | 2.5 Sq.mm | Each | 6.2 | 1
12.4.3 | 4.0 Sq.mm | Each | 7.2 | 1
12.4.4 | 6.0 Sq.mm | Each | 8.7 | 2
12.4.5 | 10.0 Sq.mm | Each | 9.5 | 2
12.4.6 | 16.0 Sq.mm | Each | 13.5 | 3
12.4.7 | 25.0 Sq.mm | Each | 21 | 4
12.4.8 | 35.0 Sq.mm | Each | 28 | 5.5
12.4.9 | 50.0 Sq.mm | Each | 45 | 9
12.4.10 | 70.0 Sq.mm | Each | 74 | 15
12.4.11 | 95.0 Sq.mm | Each | 97 | 19
12.4.12 | 120.0 Sq.mm | Each | 143 | 28
12.5 | Supply, Fabricating & installing following sizes of perforated Hot dipped Galvanized iron cable tray ( Galvanized thickness not less then 50 microns) with perforation not more then 17.5% in convenient section including horizontal and vertical bends, reducers tees,cross members and other accessories as required and duly suspended from the ceiling with GI suspenders including GI bolts & nuts , fastners, supports etc. as required.
12.5.1 | 100mm x 50mm x 1.6mm | Mtr | 488 | 63
12.5.2 | 150mm x 50mm x 1.6mm | Mtr | 598 | 77
12.5.3 | 225mm x 50mm x 1.6mm | Mtr | 780 | 100
12.5.4 | 300mm x 50mm x 1.6mm | Mtr | 957 | 123
12.5.5 | 375mm x 50mm x 2.0mm | Mtr | 1411 | 181
12.5.6 | 450mm x 50mm x 2.0mm | Mtr | 1633 | 209
12.5.7 | 600mm x 50mm x 2.0mm | Mtr | 2079 | 267
12.5.8 | 300mm x 62.5mm x 2.0mm | Mtr | 1262 | 162
12.5.9 | 375mm x 62.5mm x 2.0mm | Mtr | 1485 | 190
12.5.10 | 450mm x 62.5mm x 2.0mm | Mtr | 1707 | 219
12.5.11 | 600mm x 62.5mm x 2.0mm | Mtr | 2152 | 276
12.5.12 | 750mm x 62.5mm x 2.0mm | Mtr | 2598 | 333
12.5.13 | 600mm x 75mm x 2.0mm | Mtr | 2227 | 343
12.5.14 | 750mm x 75mm x 2.0mm | Mtr | 406 | 52
12.6 | Supply, Fabricating & installing following sizes of perforated Powder coated MS cable tray with perforation not more then 17.5% in convenient section including horizontal and vertical bends, reducers tees,cross members and other accessories as required and duly suspended from the ceiling with GI suspenders including GI bolts & nuts , fastners, supports etc. as required.
12.6.1 | 100mm x 50mm x 1.6mm | Mtr | 406 | 52
12.6.2 | 150mm x 50mm x 1.6mm | Mtr | 509 | 65
12.6.3 | 225mm x 50mm x 1.6mm | Mtr | 660 | 85
12.6.4 | 300mm x 50mm x 1.6mm | Mtr | 813 | 104
12.6.5 | 375mm x 50mm x 2.0mm | Mtr | 1206 | 155
12.6.6 | 450mm x 50mm x 2.0mm | Mtr | 1395 | 179
12.6.7 | 600mm x 50mm x 2.0mm | Mtr | 1777 | 228
12.6.8 | 300mm x 62.5mm x 2.0mm | Mtr | 1078 | 138
12.6.9 | 375mm x 62.5mm x 2.0mm | Mtr | 1268 | 163
12.6.10 | 450mm x 62.5mm x 2.0mm | Mtr | 1460 | 187
12.6.11 | 600mm x 62.5mm x 2.0mm | Mtr | 1839 | 236
12.6.12 | 750mm x 62.5mm x 2.0mm | Mtr | 2219 | 285
12.6.13 | 600mm x 75mm x 2.0mm | Mtr | 1902 | 244
12.6.14 | 750mm x 75mm x 2.0mm | Mtr | 2282 | 293
12.7 | Supply, Fabricating & installing following sizes of Hot dipped Galvanized iron Ladder type cable tray ( Galvanized thickness not less then 50 microns) with rungs at span of 250mm including horizontal and vertical bends, reducers tees,cross members and other accessories as required and duly suspended from the ceiling/wall with M.S. suspenders etc. as required.
12.7.1 | 100mm x 50mm x 1.6mm | Mtr | 392 | 50
12.7.2 | 150mm x 50mm x 1.6mm | Mtr | 490 | 63
12.7.3 | 225mm x 50mm x 1.6mm | Mtr | 638 | 82
12.7.4 | 300mm x 50mm x 1.6mm | Mtr | 784 | 101
12.7.5 | 375mm x 50mm x 2.0mm | Mtr | 1109 | 142
12.7.6 | 450mm x 50mm x 2.0mm | Mtr | 1284 | 165
12.7.7 | 600mm x 50mm x 2.0mm | Mtr | 1772 | 227
12.7.8 | 300mm x 62.5mm x 2.0mm | Mtr | 1077 | 138
12.7.9 | 375mm x 62.5mm x 2.0mm | Mtr | 1266 | 162
12.7.10 | 450mm x 62.5mm x 2.0mm | Mtr | 1456 | 187
12.7.11 | 600mm x 62.5mm x 2.0mm | Mtr | 1836 | 235
12.7.12 | 750mm x 62.5mm x 2.0mm | Mtr | 2216 | 284
12.7.13 | 600mm x 75mm x 2.0mm | Mtr | 1899 | 244
12.7.14 | 750mm x 75mm x 2.0mm | Mtr | 2279 | 292
12.8 | Supplying and fixing of CE certified and UL listed GI wire mesh cable tray made from spot welded steel wire hot dipped galvanised between 60 and 80 microns of zinc as per BS 729 including horizontal and vertical bends, reducers, tees, cross members and other OEM made accessories like wall clamp, hold down clamps, Earthing terminal, brackets as required, and duly suspended from the ceiling with electro-zinc coated TF rods, etc. as required of following sizes.
12.8.1 | 100 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 516 | 66
12.8.2 | 150 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 645 | 83
12.8.3 | 200 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 842 | 108
12.8.4 | 300 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 1031 | 132
12.8.5 | 400 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 1633 | 209
12.8.6 | 500 mm x 50 mm x 3.5 - 5.9 mm | Mtr | 1891 | 242
12.8.7 | 100 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 774 | 99
12.8.8 | 150 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 903 | 116
12.8.9 | 200 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 1031 | 132
12.8.10 | 300 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 1289 | 165
12.8.11 | 400 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 1547 | 198
12.8.12 | 500 mm x 100 mm x 3.5 - 5.9 mm | Mtr | 1805 | 231
12.9 | Supply and fixing following size of Pre Galvanized (275 GSM) floor raceways / Under floor trunking with/ without partion, including common cover, joint sleeve, cross over junction Box etc. as required.
12.9.1 | 75 mm x 25 mm x 1.5 mm | Mtr | 736 | 121
12.9.2 | 100 mm x 25 mm x 1.5 mm | Mtr | 895 | 147
12.9.3 | 150 mm x 25 mm x 1.5 mm | Mtr | 1221 | 200
12.9.4 | 250 mm x 25 mm x 1.5 mm | Mtr | 1866 | 306
12.9.5 | 300 mm x 25 mm x 1.5 mm | Mtr | 2186 | 358
12.9.6 | 75 mm x 38 mm x 1.5 mm | Mtr | 825 | 135
12.9.7 | 100 mm x 38 mm x 1.5 mm | Mtr | 384 | 161
12.9.8 | 150 mm x 38 mm x 1.5 mm | Mtr | 1304 | 214
12.9.9 | 250 mm x 38 mm x 1.5 mm | Mtr | 1945 | 319
12.9.10 | 300 mm x 38 mm x 1.5 mm | Mtr | 2269 | 372
12.9.11 | 150 mm x 38 mm x 2.0 mm with 2 Compartment | Mtr | 1820 | 298
12.9.12 | 250 mm x 38 mm x 2.0 mm with 3 Compartment | Mtr | 2816 | 462
12.9.13 | 300 mm x 38 mm x 2.0 mm with 3 Compartment | Mtr | 3207 | 562
12.10 | Supply and fixing following Pre Galvanized (275 GSM) Adjustable Junction Box for floor raceways / Under floor trunking etc. as required.
12.10.1 | Junction Box 200 mm x 200 mm x 40-75 mm with Galvanized Lid | Mtr | 5607 | 919
12.10.2 | Junction Box 250 mm x 250 mm x 40-75 mm with Galvanized Lid | Mtr | 7013 | 1150
12.10.3 | Junction Box 300 mm x 300 mm x 40-75 mm with Galvanized Lid | Mtr | 8425 | 1381
12.10.4 | Junction Box 350 mm x 350 mm x 40-75 mm with Galvanized Lid | Mtr | 9885 | 1681
12.10.5 | Junction Box 250 mm x 250 mm x 40-75 mm with stainless steel Lid | Mtr | 9786 | 1604
12.10.6 | Junction Box 300 mm x 300 mm x 40-75 mm with stainless steel Lid | Mtr | 11847 | 1942
12.10.7 | Junction Box 350 mm x 350 mm x 60-120 mm with stainless steel Lid | Mtr | 13852 | 2271
12.11 | S & Making Heat shrinkable type Tubular sleeve version outdoor straight through joint for following size of PVC/ XLPE insulated aluminium conductor cable of 1.1 KV grade as required.
12.11.1 | 1 x 25 sq.mm-50 sq.mm | Set | 2008 | 258
12.11.2 | 1 x 70 sq.mm-150 sq.mm | Set | 3244 | 416
12.11.3 | 1 x 185 sq.mm-300 sq.mm | Set | 4190 | 537
12.11.4 | 1 x 400 sq.mm | Set | 4526 | 580
12.11.5 | 1 x 500 sq.mm | Set | 5096 | 653
12.11.6 | 1 x 630 sq.mm | Set | 5215 | 669
12.11.7 | 1 x 800 sq.mm | Set | 5671 | 727
12.11.8 | 1 x 1000 sq.mm | Set | 6864 | 880
12.11.9 | 2 x 1.5 sq.mm-6 sq.mm | Set | 591 | 76
12.11.10 | 2 x 10.0-16.0 sq.mm | Set | 1530 | 196
12.11.11 | 2 x 25.0 sq.mm-50 sq.mm | Set | 2536 | 325
12.11.12 | 2 x 70.0 sq.mm-150 sq.mm | Set | 4478 | 574
12.11.13 | 2 x 185.0 sq.mm-300 sq.mm | Set | 8506 | 1091
12.11.14 | 2 x 400 sq.mm | Set | 9102 | 1167
12.11.15 | 2 x500 sq.mm | Set | 9775 | 1253
12.11.16 | 3/3.5/4 x 1.5 sq.mm-6 sq.mm | Set | 970 | 124
12.11.17 | 3/3.5/4 x 10.0-16.0 sq.mm | Set | 1730 | 222
12.11.18 | 3/3.5/4 x 25.0 sq.mm-50 sq.mm | Set | 3209 | 411
12.11.19 | 3/3.5/4 x 70.0 sq.mm-150 sq.mm | Set | 4924 | 631
12.11.20 | 3/3.5/4 x 185.0 sq.mm-300 sq.mm | Set | 9110 | 1168
12.11.21 | 3/3.5/4 x 400 sq.mm | Set | 9624 | 1234
12.11.22 | 3/3.5/4 x500 sq.mm | Set | 11341 | 1454
12.12 | S/F cable route marker with 10cm x 10cm x 5mm thick or 10 cm dia. G.I.plate with inscription thereon, bolted/welded to 35mm x 35mm x 5mm angle iron, 60cm long and fixing the same in ground in C C ( 1:3:6 ) as required | Each | 375 | 48
12.13 | P / L of Double wall corrugated HDPE pipe confirming to IS : 16205 P-24, Stiffness Class 750 N, Externally corrugated and having smooth surface inside with HDPE Coupler, Elbow, Tee at required Depth below the ground for laying cable of following Nominal Outer dia. MFR Test report from NABL accrediated is to be submitted.(Excavation of trench, CC Haunching, Back filling of Earth with compaction is to be Paid Extra).
12.13.1 | 50 mm | Mtr | 72 | 9
12.13.2 | 63 mm | Mtr | 88 | 11
12.13.3 | 75 mm | Mtr | 115 | 15
12.13.4 | 90 mm | Mtr | 165 | 21
12.13.5 | 110 mm | Mtr | 214 | 27
12.13.6 | 120 mm | Mtr | 246 | 32
12.13.7 | 160 mm | Mtr | 361 | 46
12.13.8 | 200 mm | Mtr | 494 | 63
12.14 | Providing and laying Non Pressure NP-3 class R.C.C. pipes confirming to IS:458 including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) etc. as required. (Excavation of trench, CC Haunching, Back filling of Earth with compaction is to be Paid Extra).
12.14.1 | 200 mm Dia. | Mtr | 543 | 107
12.14.2 | 250 mm dia. | Mtr | 698 | 107
12.14.3 | 300 mm dia | Mtr | 892 | 176
12.14.4 | 450 mm dia. | Mtr | 1707 | 336
12.15 | labour charges for Excavating trenches of required width for pipes dressing of sides, ramming of bottoms, depth up to 1.5 Mtr. including taking out the excavated soil, and then returning the soil as required in layers not exceeding 20cm in depth including consolidating each deposited layer by ramming, watering etc. and disposal of surplus excavated soil as directed within a lead of 50 Mtr.:
12.15.1 | All kind of Soils | Cum |  | 261
12.15.2 | Hard Rocks | Cum |  | 356
Note:
1 | Size of cable trays shall be determined by following procedure:
a. | Calculate the diameter(D) of the cross section of cable.
b. | To calculate width of the cable tray for single core cables spacing between the cables should be 2D and between the extreme end cables and cable tray should be D/2 and then add 20 % margin
c. | To calculate width of the cable tray for multi core cables spacing between the cables should be D and between the extreme end cables and cable tray should be D/2 and then add 20 % margin
d. | Height of the cable tray should be greater than the diameter of the biggest size cable.

## Ch 13 HT cable & terminations
Chapter E - 13
H T Cables & Accessories
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
13.1 | Providing & Laying XLPE insulated three core Armoured Aluminium cable for working voltage 11 K.V.(E) confirming IS :7098 P - 2 with H4- Grade electrolytic aluminium conductor confirming to IS: 8130 class-2 of purity >99.6 %, Insulation Screening: Extruded Semiconducting Compound followed by helically wrapped Copper Tape, round / flat strip armouring of cables , Inner / outer sheath PVC type ST-2 confirming to IS:5831 in existing RCC pipe / Hume Pipe/ Stoneware Pipe/ PVC pipe/ open duct/cable trench / Cable tray (with cable tie) including testing etc. as required of following size.
13.1.1 | 3 core 95.0 Sq.mm | Mtr | 988 | 100
13.1.2 | 3 core 120.0 Sq.mm | Mtr | 1137 | 111
13.1.3 | 3 core 150.0 Sq.mm | Mtr | 1283 | 133
13.1.4 | 3 core 185.0 Sq.mm | Mtr | 1488 | 144
13.1.5 | 3 core 240.0 Sq.mm | Mtr | 1783 | 167
13.1.6 | 3 core 300.0 Sq.mm | Mtr | 2106 | 189
13.2 | Providing & Laying XLPE insulated three core Armoured Aluminium cable for working voltage 33 K.V.(E) confirming IS :7098 P - 2 with H4- Grade electrolytic aluminium conductor confirming to IS: 8130 class-2 of purity >99.6 %, Insulation Screening: Extruded Semiconducting Compound followed by helically wrapped Copper Tape, round / flat strip armouring of cables , Inner / outer sheath PVC type ST-2 confirming to IS:5831 in existing RCC / Hume / Stoneware / PVC pipe/ open duct/cable trench / Cable tray (with cable tie) including testing etc. as required of following size.
13.2.1 | 3 core 150.0 Sq.mm | Mtr | 1773 | 167
13.2.2 | 3 core 185.0 Sq.mm | Mtr | 1986 | 194
13.2.3 | 3 core 240.0 Sq.mm | Mtr | 2291 | 222
13.2.4 | 3 core 300.0 Sq.mm | Mtr | 2620 | 250
13.3 | Excavation of trench of size 120 cm (Depth) x 35 cm(Width) for Laying of suitable no. of HT cable( Inter spacing between cables should not be less than 2 D) in ground with following procedure:- (a) Make a river sand bed of height 125 mm along the trench, (b) Lay the cable in the middle of the trench, (c) Provide river sand bed of height 125 mm on top of the cable. (d) Lay the protective Common burnt clay F.P.S. Bricks of Class designation 75 / Sand stone slabs of 50 mm thickness and 225 mm wide just above the sand bed vertically across the cable ( Approx. 9 no. Bricks per Mtr.), (e) Backfill the excavated soil leaving 300 mm from the Ground level, (f)Lay the Cable warning tape and again back-fill the remaining portion of the trench upto the ground level and compacting the earth | Mtr | 185 | 91
13.4 | Add Extra in Item no. 13.3 if Excavation done in Hard Rock / CC road / TAR Road and making Good the same | Mtr |  | 70
13.5 | Add Extra for Laying of one number additional XLPE power cable of 11/33 KV (Earthed) voltage grade direct in ground in the same trench in one tier horizontal formation including excavation of trench of size additional 20 cm in width, with procedure as per following points:- (a) Make a river sand bed of height 125 mm along the trench, (b) Lay another cable in middle of trench in such manner that spacing between another cable is 20 cm, (c) Provide sand bed of height 125 mm on top of the cable. (d) Lay the protective Common burnt clay F.P.S. Bricks of Class designation 75 / Sand stone slabs of 50 mm thickness and 225 mm wide just above the sand bed vertically across the cable ( Approx. 9 no. Bricks per Mtr.) (e) Backfill the excavated soil leaving 300 mm from the Ground level. (f)Lay the Cable warning tape and again back-fill the remaining portion of the trench upto the ground level and compacting the earth | Mtr | 133 | 60
13.6 | Add Extra in Item no. 13.5 if Excavation done in Hard Rock / CC road / TAR Road and making Good the same | Mtr |  | 39.996
13.7 | Providing & making heat shrinkable type indoor/outdoor/straight through terminations/ joint kit suitable for 11 KV / 33 KV (Earthed) cable with required components, prepration of cable ends. Type test report should be as per IS13573:2011 including testing etc. as required of following sizes.
13.7.1 | 11 KV End Termination Kit Indoor type
13.7.1.1 | 3 core up to 35 Sqmm | Each | 2787 | 833
13.7.1.2 | 3 core 50/70/95 Sq.mm | Each | 3550 | 1111
13.7.1.3 | 3 core 120/150/185 Sq.mm | Each | 4198 | 1389
13.7.1.4 | 3 core 240/300 Sq.mm | Each | 4984 | 1667
13.7.1.5 | 3 core 400 Sq.mm | Each | 5655 | 1944
13.7.2 | 11 KV End Termination Kit Outdoor type
13.7.2.1 | 3 core up to 35 Sqmm | Each | 3631 | 1111
13.7.2.2 | 3 core 50/70/95 Sq.mm | Each | 4429 | 1389
13.7.2.3 | 3 core 120/150/185 Sq.mm | Each | 5573 | 1667
13.7.2.4 | 3 core 240/300 Sq.mm | Each | 6256 | 1944
13.7.2.5 | 3 core 400 Sq.mm | Each | 6822 | 2222
13.7.3 | 11 KV Straight Through Joint Kit
13.7.3.1 | 3 core up to 35 Sq.mm | Each | 6302 | 1667
13.7.3.2 | 3 core 50/70/95 Sq.mm | Each | 7019 | 1944
13.7.3.3 | 3 core 120/150/185 Sq.mm | Each | 8660 | 2222
13.7.3.4 | 3 core 240/300 Sq.mm | Each | 9863 | 2500
13.7.3.5 | 3 core 400 Sq.mm | Each | 10857 | 2778
13.7.4 | 33 KV End Termination Kit Indoor type
13.7.4.1 | 3 core 95 Sq.mm | Each | 5493 | 1667
13.7.4.2 | 3 core 120/150/185 Sq.mm | Each | 6140 | 2222
13.7.4.3 | 3 core 240/300/400 Sq.mm | Each | 6903 | 2222
13.7.5 | 33 KV End Termination Kit Outdoor type
13.7.5.1 | 3 core 95 Sq.mm | Each | 6464 | 2222
13.7.5.2 | 3 core 120/150/185 Sq.mm | Each | 7574 | 2778
13.7.5.3 | 3 core 240/300/400 Sq.mm | Each | 8639 | 3333
13.7.6 | 33 KV Straight Through Joint Kit
13.7.6.1 | 3 core 95/120/150 Sq.mm | Each | 12938 | 3333
13.7.6.2 | 3 core 185/240/300 Sq.mm | Each | 15551 | 3889
13.7.6.3 | 3 core 400 Sq.mm | Each | 17494 | 4444
Note:
1 | OEM must ensure that the cable is tested for complaince, through their in house laboratory accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and testing procedure as per IS:10810.
2 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 14 Earthing & LA
Chapter E 14
Earthing
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
14.1 | Pipe Earthing as per IS:3043- 1987 with 3.0 Mtr. Long, 40 mm dia. ' B ' class G.I. Pipe IS: 1239 (Part-1) 2004, Equivalent to BS : 1387 with perforated holes of 12 mm dia ,including all accessories like nut, bolts, reducer, nipple, wire meshed funnel, Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm and embodying the pipe complete with alternate layers salt and coke/ charcoal, testing of earth resistance for value of 5 ohms or less as required. | Set | 4040 | 1222
14.2 | Plate Earthing as per IS:3043 with Hot dipped G.I. Earth plate of size 600mm x 600mm x 6.0mm by embodying 3 to 4 mtr. below the ground level with 20 mm dia. G.I. 'B' class watering Pipe ,including all accessories like nut, bolts, reducer, nipple, wire meshed funnel, Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm. and embodying the pipe complete with alternate layers salt and coke/ charcoal, testing of earth resistance for value of 5 ohms or less as required. | Set | 6779 | 2000
14.3 | Plate Earthing as per IS:3043 with copper Earth plate of purity >95% of size 600mm x 600mm x 3.0mm by embodying 3 mtr. below the ground level with 20 mm dia. G.I. 'B' class watering Pipe ,including all accessories like nut, bolts, reducer, nipple, wire meshed funnel, Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm. and embodying the pipe complete with alternate layers salt and coke/ charcoal, testing of earth resistance for value of 5 ohms or less as required. | Set | 15766 | 2000
14.4 | SITC of Copper Bonded rod Earthing with high tensile strength (more than 600 N / sq.mm low carbon steel rod molecularly bonded with Copper thickness (250 microns) and confirming to UL 467 of following size and length and as per point mentioned (a), (b), [c), (d), (e) below :-
(a) Bore a hole of dia. 100 mm of required length, Place the rod in the centre of Hole
(b)Earth enhancing compound to ensure the moisture content and electrical conductivity, 25 kg for 3000 mm. The compound shall be tested form NABL accredited lab for low resistivity (less than 0.12 Ohm - meter) & high conductivity in nature with carbon as a major content in accordance with IEC 62561-7
© Connect the rod with copper Strip/Conductor/Wire with suitable clamp made from tinned copper and SS 304 Bolt
(d) Place Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm.
(e) Testing of earth resistance for value of 5 ohms or less as required.
(f) Test certificates for confirming above standards from OEM is mandatory.
14.4.1 | 17.2 mm thick and 3 Mtr. Long | Set | 7157 | 1667
14.4.2 | 25 mm thick and 3 Mtr. Long | Set | 8428 | 1667
14.5 | SITC of Strip in Pipe Earthing using hot-dip galvanized 'B' class G.I. pipe, as secondary conductor. The system shall incorporate a crystalline conductive compound between the primary and secondary conductors to enhance conductivity and long-term stability. of following size and length and as per point mentioned (a), (b), [c), (d), (e) (f) as below
(a) Bore a hole of dia. 150 mm of required length, Place the rod in the centre of Hole
(b)Earth enhancing compound to ensure the moisture content and electrical conductivity, 30 kg for 3000 mm. 20 Kg. for 2000 mm The compound shall be tested form NABL accredited lab for low resistivity (less than 0.12 Ohm - meter) & high conductivity in nature with carbon as a major content in accordance with IEC 62561-7
© Connect the Strip Terminal (110 mm long) with copper Strip/Conductor/Wire with suitable clamp made from tinned copper and SS 304 Bolt
(d) Place Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm.
(e) Testing of earth resistance for value of 5 ohms or less as required.
(f) Test certificates for confirming above standards from OEM is mandatory.
14.5.1 | Outer Pipe - 76 mm dia GI pipe , Inner Conductor- GI strip 50x6 mm Length 3meter. Terminal 50x6mm GI. | Set | 7134 | 1667
14.5.2 | Outer Pipe - 76 mm dia GI pipe , Inner Conductor- GI strip 50x6 mm Length 2 meter.Terminal 50x6mm GI. | Set | 5234 | 1333
14.5.3 | Outer Pipe - 76 mm dia GI pipe , Inner Conductor- Copper strip 25x3 mm Length 3meter. Terminal 50x6mm Copper. | Set | 9381 | 1667
14.5.4 | Outer Pipe - 76 mm dia GI pipe , Inner Conductor- Copper strip 25x3 mm Length 2 meter.Terminal 50x6mm Copper. | Set | 6753 | 1333
14.5.5 | Outer Pipe - 56 mm dia GI pipe , Inner Conductor- GI strip 25x3 mm Length 3meter. Terminal 40x5 mm GI. | Set | 5613 | 1667
14.5.6 | Outer Pipe - 56 mm dia GI pipe , Inner Conductor- GI strip 25x3 mm Length 2 meter. Terminal 40x5 mm GI. | Set | 4110 | 1333
14.5.7 | Outer Pipe - 56 mm dia GI pipe , Inner Conductor- Copper strip 25x3 mm Length 3meter. Terminal 40x5 mm Copper. | Set | 7852 | 1667
14.5.8 | Outer Pipe - 56 mm dia GI pipe , Inner Conductor- Copper strip 25x3 mm Length 2 meter. Terminal 40x5 mm Copper. | Set | 6493 | 1555
14.6 | Supply & Laying following size earth strip in horizontal or vertical run in surface by means of Earth strip DMC Insulator including riveting/ soldering/ welding, Jointing shall be done by overlapping double the width of strip and with 2 set of Brass (for Cu strip) / GI (for GI Strip) nut bolt & spring washer spaced at 50cm making connection etc. as required.
14.6.1 | 20mm x 3mm copper strip | Mtr. | 851 | 56
14.6.2 | 25mm x 3mm copper strip | Mtr. | 1129 | 67
14.6.3 | 25mm x 5mm copper strip | Mtr. | 1612 | 89
14.6.4 | 30mm x 5 mm copper strip | Mtr. | 2005 | 100
14.6.5 | 40mm x 6mm copper strip | Mtr. | 3181 | 133
14.6.6 | 50mm x 6mm copper strip | Mtr. | 4231 | 167
14.6.7 | 20mm x 3mm tinned copper strip | Mtr. | 927 | 56
14.6.8 | 25mm x 3mm tinned copper strip | Mtr. | 1230 | 67
14.6.9 | 25mm x 5mm tinned copper strip | Mtr. | 1757 | 89
14.6.10 | 30mm x 5 mm tinned copper strip | Mtr. | 2187 | 100
14.6.11 | 40mm x 6mm tinned copper strip | Mtr. | 3472 | 133
14.6.12 | 50mm x 6mm tinned copper strip | Mtr. | 4618 | 167
14.6.13 | 20mm x 3mm G.I. ( Hot Dipped ) Strip | Mtr. | 129 | 56
14.6.14 | 25mm x 3mm G.I. ( Hot Dipped ) Strip | Mtr. | 158 | 67
14.6.15 | 25mm x 6mm G.I. ( Hot Dipped ) Strip | Mtr. | 272 | 89
14.6.16 | 32mm x6mm G.I. ( Hot Dipped ) Strip | Mtr. | 330 | 111
14.6.17 | 50mm x 6mm G.I. ( Hot Dipped ) Strip | Mtr. | 532 | 167
14.7 | Supply & Laying following size earth wire in horizontal or vertical run in ground/surface/recess including riveting, soldering, saddles, making connection with GI/Cu purity purity >95% thimble etc. as required.
14.7.1 | 6 SWG tinned copper Wire | Mtr. | 276 | 22
14.7.2 | 8 SWG tinned copper Wire | Mtr. | 194 | 17
14.7.3 | 10 SWG tinned copper. Wire | Mtr. | 126 | 11
14.7.4 | 6 SWG copper Wire | Mtr. | 254 | 22
14.7.5 | 8 SWG copper Wire | Mtr. | 179 | 17
14.7.6 | 10 SWG copper. Wire | Mtr. | 116 | 11
14.7.7 | 6 SWG G.I. ( Hot Dipped ) Wire | Mtr. | 44 | 22
14.7.8 | 8 SWG G.I. ( Hot Dipped ) Wire | Mtr. | 32 | 17
14.7.9 | 10 SWG G.I. ( Hot Dipped ) Wire | Mtr. | 21 | 11
14.7.10 | 16 Sq.mm Copper coated steel stranded conductor (Wt. 130 Kg/Km) | Mtr. | 54 | 11
14.7.11 | 25 Sq.mm Copper coated steel stranded conductor ( Wt. 200Kg/Km) | Mtr. | 83 | 17
14.8 | Supply & Laying following size' B ' class , G.I. Pipe confirming to IS : 1239 P - 1 ( 2004 ) with accessories like bend, socket etc. for laying earth conductor/ strip / cable in ground/ surface/ recess as required. (Earth Excavation will be Paid Extra)
14.8.1 | 15 mm dia. | Mtr. | 201 | 44
14.8.2 | 20 mm dia. | Mtr. | 255 | 56
14.8.3 | 25 mm dia. | Mtr. | 337 | 56
14.8.4 | 32mm dia | Mtr. | 437 | 83
14.8.5 | 40 mm dia. | Mtr. | 515 | 111
14.8.6 | 50 mm dia. | Mtr. | 705 | 139
14.8.7 | 65 mm dia. | Mtr. | 909 | 167
14.8.8 | 80 mm dia. | Mtr. | 1102 | 194
14.8.9 | 100 mm dia. | Mtr. | 1536 | 222
14.8.10 | 150 mm dia. | Mtr. | 2341 | 278
14.9 | Mesh earthing as per IS:3043 with Hot dipped galvanized earth strip of size 25 mm x 6 mm to form a mesh of size 1000 mm x 1000 mm in horizontal formation to create equal sections of 200 mm x 200 mm by means of welding and embodying 1 mtr. Below the ground level, refilling the pit by alternative layers of charcoal & salt up to 500 mm with 20 mm dia. GI 'B' class watering pipe, wire mesh funnel and 300 mm x 300 mm size masonary chamber with lockable 6 mm thick MS sheet cover hinged with suitable angle iron frame testing of earth resistance for value of 5 ohms or less as required. | Each | 6980 | 2222
14.10. | P & F of Heavy duty weather proof poly-propylene earth inspection chamber as per requirement of IS/IEC 62305 and tested as per IEC 62561-5 with lockable Jam free lid suitable for safe working load 60 kN of round / square size 250 mm, and Height 250 to 300 mm. | Each | 1209 | 111
14.11 | S & F of Earth Bar with Disconnecting link Made out from 50 mm x 6 mm copper purity purity >95% /GI strip pre fitted on epoxy powder coated metal base mounted on hexagonal SMC Insulators of following Size.
14.11.1 | 400 mm , 6 Way Copper | Each | 1845 | 111
14.11.2 | 600 mm , 10 Way Copper | Each | 2710 | 167
14.11.3 | 400 mm , 6 Way GI | Each | 805 | 111
14.11.4 | 600 mm , 10 Way GI | Each | 1207 | 167
14.12 | Providing & Making of Exothermic joint in Tee / Square / Straight through joint in Strip for permanently bonding of copper to copper or copper to GI including required exothermic jointing kit comprising of graphite mould, weld powder, tools etc. as required. | per Joint | 1194.9383 | 178
14.13 | Supply, installation, testing & commissioning of following size & Material Lightning protection system accessories meeting requirement of IS/IEC 62305 and tested as per IEC 62561-2 / IS 18925 (Part 1-7) : 2025 as required.
14.13.1 | 100 microns Copper bonded steel Solid round conductor 10 mm dia. | Mtr. | 433 | 89
14.13.2 | Aluminium alloy Solid round conductor 8 mm dia. | Mtr. | 174 | 56
14.13.3 | SS 304 Solid round conductor 10 mm dia. | Mtr. | 556 | 111
14.13.4 | Alluminium alloy Vertical Air termination 16/10 mm with base mounted on 2000 mm 40 mm GI pipe as mast | Set | 3330 | 556
14.13.5 | Alluminium alloy Vertical Air termination 16/10 mm with base mounted on 3000 mm 40 mm GI pipe as mast | Set | 4532 | 833
14.13.6 | Alluminium alloy Vertical Air termination 16/10 mm with base mounted on 5000 mm 56/40 mm GI pipe as mast | Set | 7793 | 1667
14.13.7 | Alluminium alloy Vertical Air termination 16/10 mm with base mounted on 5000 mm 76/56/40 mm GI pipe as mast | Set | 9527 | 1667
14.13.8 | Alluminium alloy Vertical Air termination 16/10 mm with SS 304 Clamp of Size 1000 mm for Wall | Set | 2323 | 389
14.13.9 | Alluminium alloy Vertical Air termination 16/10 mm with SS 304 Clamp of Size 2000 mm for Wall | Set | 3849 | 556
14.13.10 | Alluminium alloy Vertical Air termination 16/10 mm with SS 304 Holder of Size 1000 mm for Parapet | Set | 2905 | 389
14.13.11 | SS 304 Clamp to join Vertical Air terminal and 8/10 mm round conductor | Each | 455.0034 | 39
14.13.12 | SS 304 Clamp to join Vertical Air terminal and 25 mm x 3 mm flat conductor | Each | 524 | 39
14.13.13 | SS 304 holder for 8/10 mm round conductor on Parapet | Each | 221 | 39
14.13.14 | SS 304 holder with Concrete base for 8/10 mm round conductor on Flat roof | Each | 268 | 83
14.13.15 | SS 304 clamp connector for 8/10 mm round conductor on metal structure | Each | 388 | 56
14.13.16 | SS 304 cross connector for 8/10 mm round conductor | Each | 372 | 39
14.13.17 | Alluminium alloy expansion piece with connector for 8/10 mm round conductor | Each | 285 | 39
14.13.18 | Alluminium alloy straight,cross & T connector for 8/10 mm round conductor | Each | 355 | 56
14.13.19 | SS 304 straight connector for 8/10 mm round conductor | Each | 285 | 39
14.13.20 | SS 304 conductor holder for 25 mm x 3 mm Flat conductor | Each | 258 | 56
14.13.21 | SS 304 holder with Concrete base for 25 mm x 3 mm Flat conductor on Flat roof | Each | 238 | 56
14.13.22 | Alluminium alloy expansion piece for 25 mm x 4 mm flat conductor | Each | 374 | 49.995
14.13.23 | SS 304 cross connector for 25 mm x 3 mm flat conductor | Each | 455 | 49.995
14.13.24 | SS 304 test joint with Polycarbonate enclosure with copper flat with 4 holes of 8/10 mm dia to connect round conductor | Each | 2158 | 556
14.13.25 | SS 304 test joint with Polycarbonate enclosure with copper flat with 4 holes of 8/10 mm dia to connect round conductor | Each | 2161 | 556
14.13.26 | SS 304 Earth stud for air terminal and 8/10 mm round conductor | Each | 2058 | 278
14.13.27 | SS 304 Equipotential Bonding rail 500 x 50 x 10 mm | Each | 7137 | 556
14.13.28 | Lightning Surge Counter designed to record and display lightning strike events. The counter shall feature a 3 digit LCD screen (0-999 events) for clear event tracking and operate on a battery powered system. | Each | 15351 | 556
14.14 | Supply, installation, and testing of an Early Streamer Emission (ESE) Air Terminal, designed and tested in accordance with NFC 17-102 standards, with Delta T ( Initiation Advance ) time tested and certified by an ILAC-accredited high-voltage test laboratory. The air terminal shall be constructed from corrosion-resistant materials to ensure durability and long-term performance. It shall be installed at the highest point of the structure and mounted on a mast of minimum 5.5 meters or as determined by the initiation advance time (ΔT) calculations, ensuring the required protection radius. The protection radius shall be determined as per NFC 17-102, based on the level of risk protection required (Levels I to IV), with proper Earthings integration for effective lightning dissipation.
14.14.1 | ES-60 Triggering Advance Time (ΔT) -60µs, Protection Radius (meters) as per Highest Risk 79 Mtr. | Each | 75088 | 1111
14.14.2 | ES-45 Triggering Advance Time (ΔT) -45µs, Protection Radius (meters) as per Highest Risk 61 Mtr. | Each | 66996 | 1111
14.14.3 | ES-30 Triggering Advance Time (ΔT) -30µs, Protection Radius (meters) as per Highest Risk 42 Mtr. | Each | 63529 | 1111
14.15 | Supply, fabrication, and installation of a galvanized iron (GI) pipe support structure ( Lightning Mast ) with a 350 mm × 350 mm base plate and 10 mm thickness for secure mounting. The mast shall support the ESE air terminal and include provisions for a guy wire clamping system to ensure stability. It shall provide a secure arrangement for fixing the air terminal and have appropriate termination point / arrangement for connection to the downconductor.
14.15.1 | Total Mast height : 3-4.5 meter | Each | 8602 | 1667
14.15.2 | Total Mast height : 5-7.5 meter | Each | 9758 | 1667
14.15.3 | Total Mast height : 8-10 meter | Each | 11492 | 1667
14.16 | Supply and installation of an 8 mm aluminum down conductor, designed for efficient dissipation of lightning currents. The conductor shall be securely fixed using corrosion-resistant clamps at appropriate intervals, ensuring a continuous, low-resistance path from the air terminal to the earthing system. The conductor length shall be determined based on actual site conditions, with all necessary accessories, including clamps, connectors, and fasteners. | Mtr. | 212 | 44

## ch 15 Fans
Chapter E -15
Fans
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
15.1 | Making of hole in wall (brick/stone) of required and placing NP-2 RCC pipe ring of required size for housing exhaust fan and making good the same, with cement plaster required of following size.
15.1.1 | Up to 457 mm size | Each | 319 | 111
15.1.2 | more than 457 mm & up to 610 mm | Each | 456 | 167
15.2 | Supply & Fixing of phenolic laminated board of 6.0 mm thick for fresh air fan/exhaust fan up to size of 300 mm on existing window frame including cost of board, cutting of hole , Nut bolts etc. as required. | Sqm | 1323 | 167
15.3 | Installation , testing and Commissioning of ceiling fan (any size) including wiring the down rod up to 30 cm with 3 x 1.5 sq.mm pvc insulated flexible copper conductor, Cotter pin, rubber grommet making connection testing etc. as required.
15.3.1 | With regulator | Each | 124 | 89
15.3.2 | Without regulator | Each | 107 | 72
15.4 | Providing & Fixing BLDC technology step regulator compatible ceiling fan, with aluminium body & aluminium blade, power factor not less then 0.9 , following service value (CMM/W) , with following air delivery , speed 350 RPM ( tolerance as per IS:374 2019 ) THD less then 10%, copper winding with class of Insulation 'F' complete with with secondary support safety cable ( steel rope), down rod up to 30 cm, cotter pin, shackle kit with 3 x 1.5 sq.mm pvc insulated flexible copper conductor making connection testing etc. as required.
15.4.1 | 1200 mm sweep with Air delivery >/= 230 CMM and Service Value 8.20 | Each | 3049 | 72
15.4.2 | 1400 mm sweep with Air delivery >/= 270 CMM and Service Value 7.70 | Each | 3268 | 89
15.4.3 | 1200 mm sweep with Air delivery >/= 215 CMM and Service Value 7.00 | Each | 2725 | 72
15.4.4 | 1400 mm sweep with Air delivery >/= 260 CMM and Service Value 6.4 | Each | 2921 | 89
15.5 | Providing & Fixing of of BLDC Technology ventilating fans , single phase with PVC impeller, ABS body, Double Ball bearing, automatic back lower shutter including making connection, testing etc. as required.
15.5.1 | 150 mm sweep with Min. Air delivery 350 Cubic meter/Hr, 2000 RPM | Each | 2153 | 72
15.5.2 | 200 mm sweep with Min. Air delivery 800 Cubic meter/Hr, 1600 RPM | Each | 2326 | 72
15.5.3 | 250 mm sweep with Min. Air delivery 1150 Cubic meter/Hr, 1300 RPM | Each | 2534 | 72
15.6 | Providing & Fixing of 400 mm Sweep BLDC technology Oscillating type Wall mounting / Pedestal type fans with Three speed, ON and OFF position, Double Wall bearing with front and back 120 or more ribs guard; Three no. blades, noise level should be <= 75 dB, including fixing with anchor bolts, making connection testing etc. as required. ( With Remote )
15.6.1 | Wall mounting type with Service value 2.0 CMM /W, Min. Air Delivery 71 CMM | Each | 4118 | 72
15.6.2 | Pedestal Type having Adjustable Height with Service value 2.6 CMM /W, Min. Air Delivery 85 CMM | Each | 5183 | 39
15.7 | Providing & Fixing of BEE Star rated copper wounded with class of Insulation 'F', double ball bearing capacitor start, aluminium body & aluminium blade ceiling fan conforming to all the performance requirements laid down in IS 374:2019 with down rod up to 30 cm with secondary support safety cable ( steel rope) , cotter pin, shackle kit with 3 x 1.5 sq.mm pvc insulated flexible copper conductor and making connection testing etc. as required.
15.7.1 | 1200 mm Sweep BEE 1 Star rated (service value >=4.0 to < 4.5 ) | Each | 1748 | 72
15.7.2 | 1200 mm Sweep BEE 2 Star rated (service value >=4.5 to < 5 ) | Each | 1875 | 72
15.7.3 | 1200 mm Sweep BEE 3 Star rated (service value >=5.0 to< 5.5 ) | Each | 2003 | 72
15.7.4 | 1400 mm Sweep BEE 1 Star rated (service value >=4.0 to < 4.5 ) | Each | 2141 | 89
15.7.5 | 1400 mm Sweep BEE 2 Star rated (service value >=4.5 to < 5 ) | Each | 2303 | 89
15.7.6 | 1200 mm Sweep BEE 1 Star rated (service value >=4.0 to < 4.5 ) with minimum Air delivery 230 CMM | Each | 2326 | 72
15.7.7 | 1400 mm Sweep BEE 1 Star rated (service value >=4.0 to < 4.5 ) with minimum Air delivery 230 CMM | Each | 2592 | 89
15.8 | Providing & Fixing of shackle (iron hook) made from 2mm nominal thick CRCA sheet and bolts (2nos) of 6mm with spring washer nut, checknut & split pin as required. | Each | 218 | 44
15.9 | Providing & Fixing of of M.S. J- hook of standard design made out of 16 mm dia. M.S. round bar and fixed with cement concrete mortar with required support as required. | Each | 206 | 44
15.10. | P & F 1.2 mm thick M.S. Recessed fan box and top lid screwed on Box, hexagonal/ round of size 130 mm dia, depth 75mm, 12 mm dia rod fan hook with 150 mm length extended on each side as required. | Each | 129 | 21
15.11 | P & F 3.0 mm thick Poly propelene plastic polished concealed fan box, squre of size (106x106) mm dia, depth 50 mm , 10 mm dia rod of MS with chrome plated with 55 mm length extended on each side as required. | Each | 110 | 18
15.12 | Providing & Fixing of of Double ball bearing, copper wounded capacitor start single phase metallic blade fresh air fan, in existing opening including cost of hardware , flexible 3 core 1.5 Sq.mm copper conductor ,making connections, testing etc. as required.
15.12.1 | 230 mm sweep, Minimum air delivery 750 Cum / hour | Each | 1482 | 72
15.12.2 | 300 mm sweep Minimum air delivery 1600 Cum / hour | Each | 1598 | 72
15.13 | Providing & Fixing of Heavy duty capacitor start, copper wound Double ball bearing 900/1400 RPM single phase Exhaust fan conforming to IS:2312 marked in existing opening including making connections testing etc. as required.
15.13.1 | 300 mm sweep(900 RPM) | Each | 2955 | 111
15.13.2 | 380 mm sweep(900 RPM) | Each | 3468 | 139
15.13.3 | 450 mm sweep(1400 RPM) | Each | 4744 | 167
15.13.4 | 600 mm sweep(900 RPM) | Each | 10070 | 222
15.14 | Providing & Fixing of ventilating fans Capacitor start, copper wounded, single phase with PVC impeller, ABS body, automatic openable louver shutter in existing opening including making connection, testing etc. as required.
15.14.1 | 150 mm sweep Minimum Air Delivery 150 Cum / hour | Each | 1343 | 83
15.14.2 | 200 mm sweep Minimum Air Delivery 450 Cum / hour | Each | 1413 | 83
15.14.3 | 250 mm sweep Minimum Air Delivery 750 Cum / hour | Each | 1609 | 83
15.15 | Providing & Fixing of Wall mounting / Pedestal type Heavy duty Air Circulator , Double ball bearing and with metal sturdy mesh guard; Aluminium alloy one piece blade and conforming to IS:2997, including fixing with anchor bolts, making connection testing etc. as required.
15.15.1 | 450 mm sweep Wall mounting and three speed regulator with Minimum Air Delivery 150 Cum. / Minute | Each | 6177 | 167
15.15.2 | 450 mm sweep Pedestal type and three speed regulator with Minimum Air Delivery 150 Cum. / Minute | Each | 77046 | 111
15.15.3 | 600 mm sweep Wall mounting with Minimum Air Delivery 270 Cum. / Minute | Each | 7907 | 278
15.15.4 | 600 mm sweep Pedestal type with Minimum Air Delivery 270 Cum. / Minute | Each | 8896 | 111
15.15.5 | 750 mm sweep Wall mounting with Minimum Air Delivery 400 Cum. / Minute | Each | 9752 | 389
15.15.6 | 750 mm sweep Pedestal type with Minimum Air Delivery 400 Cum. / Minute | Each | 10630 | 111
15.16 | Providing & Fixing of 450 mm Sweep Oscillating type Wall mounting / Pedestal type fans with Three speed, ON and OFF position, Sintered Iron bush oil impregnated, with metal front and back 120 or more ribs guard; Three no. Aluminium blades, minimum Air delivery 100 Cum. / Minute , Minimum Service Value 1.11 Cum./min/watt, noise level should be <= 75 dB, power consumption <= 120 watts, motor protection through thermal overload protection device, including fixing with anchor bolts, making connection testing etc. as required.
15.16.1 | Wall mounting type with Adjustable Vertical Angle | Each | 4848 | 167
15.16.2 | Pedestal Type with Adjustable Height | Each | 5266 | 111
15.17 | Providing & Fixing of extra down rod of 15 mm dia . ERW (Electrical resistance welded ) of 1.6mm nominal thick medium duty steel pipe including cutting, threading, drilling, fixing quarter pin etc as required. | Mtr. | 218 | 44
15.18 | Numbering of ceiling fans/ fixtures with approved enamel paint etc as required. | Each | 28 | 17
15.19 | P & F of Gravity Louver shutter of superior quality made out of frame of 18 swg M.S. sheet & Louvers made from 24 swg MS Sheet with enamel paint including cost of nuts, bolts, etc as required.
15.19.1 | Up to 380 mm size | Each | 286 | 83
15.19.2 | above 380 mm size | Each | 372 | 83
15.20. | P & F of Wall cowl with Bird Screen Suitable for Outside Wall of Exhaust Fan Opening of following size and made out from 24 SWG GI sheet as per instructions of Engineer in charge including fixing with suitable fasteners etc. as required.
15.20.1 | Suitable for 300 mm sweep Exhaust Fan | Each | 1036 | 111
15.20.2 | Suitable for 380 mm sweep Exhaust Fan | Each | 1496 | 167
15.20.3 | Suitable for 450 mm sweep Exhaust Fan | Each | 2002 | 222
15.21 | S & F Extruded Aluminium Fresh Air / External Weather Louver, Small Format type with 38 mm flange width & 50 mm depth. finish - powder coated off white with aluminium mesh of required size. | Sqm | 8624 | 167
15.22 | SITC of single phase 230 V, 50 Hz, Permanent Magnet synchronous motorised (PMSM) High volume low speed (HVLS) fan comprising of aviation grade extruded Alluminium alloy 6063-T grade aerofil 5/6 blade, Suitable Hanging bracket with extension tube for suitable clearance from blade to ceiling, Fastners, Nut bolts, PVC coated GI guy Wire rope, VFD control panel, sound level 45-50 dB, suitable cable from control panel to Fan motor of following sizes.
15.22.1 | 8' dia, floor to fan blade height 12-15 ft,. Area coverage 4000 sq.ft, air delivery 136000 cfm, 110 RPM | Set | 170712 | 8888
15.22.2 | 10' dia, floor to fan blade height 14-17 ft,. Area coverage 5500 sq.ft, air delivery 150000 cfm, 100 RPM | Set | 184493 | 11110
15.22.3 | 12' dia, floor to fan blade height 16-18 ft,. Area coverage 7000 sq.ft, air delivery 164000 cfm, 95 RPM | Set | 198274 | 13332
15.22.4 | 16' dia, floor to fan blade height 18-22 ft,. Area coverage 10000 sq.ft, air delivery 220000 cfm, 80 RPM | Set | 240168 | 17776
15.22.5 | 20' dia, floor to fan blade height 22-27 ft,. Area coverage 13500 sq.ft, air delivery 280000 cfm, 65 RPM | Set | 259176 | 22220
15.22.6 | 24' dia, floor to fan blade height 27-30 ft,. Area coverage 18500 sq.ft, air delivery 380000 cfm, 55 RPM | Set | 286738 | 26664
Note:
1 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 16 Water Heaters
Chapter E - 16
Water Heaters
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
16.1 | Providing & Fixing of Vertical(BEE 5 star rated) / Horizontal( BEE 3 star rated) storage water heater with outer casing made of Engineering Plastic sheet (Upto 25 Ltr) / Metal rust proof Body (35 & 50 Ltr), Glass - line / Titanium Enamel coated Pressure Pump Compatible 8 bar pressure Inner tank, Glass Line Coated , mineral filled heating element, stem type, snap action adjustable thermostat , Dual indicating lamps Injected PUF insulation, Multi Function Valve etc. as required held in position with 2/4 no. 10/12 mm anchor Fastener, duly wired with 3 core 2.5/4.0 Sqmm PVC insulated & sheathed copper conductor and 16 A/25A three pin plug top , including making inlet, outlet Flexible alloy connection, testing etc. as required.
16.1.1 | 6 Ltr. | Each | 7308 | 500
16.1.2 | 10 Ltr. | Each | 8302 | 500
16.1.3 | 15 Ltr. | Each | 9458 | 500
16.1.4 | 25 Ltr. | Each | 10664 | 556
16.1.5 | 35 Ltr. | Each | 12839 | 778
16.1.6 | 50 Ltr. | Each | 16328 | 1111
16.2 | Providing & Fixing of stem type ISI marked (IS 3017 / 85) snap action adjustable thermostat for storage water heater including making connection testing etc. complete in all respect. | Each | 597 | 110
16.3 | Providing & Fixing of stem type ISI marked (IS 3017 / 85) , snap action bipolar adjustable thermostat with built in auto thermal cut out for storage water heater including making connection testing etc. complete in all respect. | Each | 839 | 111
16.4 | Providing & Fixing 2 / 3 KW nickle plated, mineral filled heating element including making connection testing etc complete in all respect. | Each | 1040 | 111
16.5 | Providing & Fixing of 2 / 3 KW Glass Line Coated , mineral filled heating element including making connection testing etc complete in all respect. | Each | 1659 | 111
16.6 | Providing & Fixing of Multi safety valve of 8.5 bar capacity with built in drain, NRV, Vacuum release, Pressure release etc. as required complete in all respect. | Each | 467 | 72
16.7 | Providing & Fixing of Twin neon indicating lamp of superior quality for storage water heater complete in all respect. | Each | 119 | 28
16.8 | Providing & Fixing of 13 mm Brass with C.P. finished ISI marked angle valve for storage water heater as required complete in all respect. | Each | 439 | 111
16.9 | Providing & Fixing of heavy duty flexible alloy pipe for storage water heater for inlet and outlet of suitable length including the cost of nuts, washers etc complete in all respect.
16.9.1 | 450 mm | Set | 536 | 111
16.9.2 | 600 mm | Set | 597 | 111
16.10 | Charges for descaling of storage water heater including replacement of Multi Function Valve as required. | P.Job | 667 | 333
16.11 | Charges for Fixing of storage water heater including 10/12 mm Anchor fasteners of suitable size, testing, carrying from store to site,etc. as required. | P.Job | 319 | 222
16.12 | Providing & Fixing of 2.0 KW twin ceremic cartridge, Withstands temperatures up to 1000 C long lasting even in hard water including making connection testing etc complete in all respect. | Each | 1021 | 111
16.13 | Supplying, Installation, Testing, Commissioning of following capacity Evacuated Tube Collector (ETC) Solar Water Heating System comprising of all glass ETC tube absorber. The inner layer of absorber shall be of solar selected absorbing coated tube, Vacuum jacket, cover glass tube, getter and getter mirror surface, as per IS 16543. The system shall have temperature gauges, strainer, 2 nos. water meters, Suitable capacity cold and hot water tank, all MS structure for installation including suitable electric control panel complete with control and power wiring, necessary pluming including piping for cold and hot water line between tank and solar water system, water heater and thermostat including non-return valve, float valve and other valve etc. as required. The various component shall have specification as A, B, C, D, E & F
A)The Absorber area i.e. the number, dimension and thickness of solar evacuated tube as per IS:16544 clause 5.4 and IS: 16543 clause 4.2
B) Boro Silicate Glass 3.3 for cover plat as per ISO: 3585.
C) The material for three target coating shall be aluminum nitrate, aluminum nitrate stainless steel and copper multi layer selecting coating as per IS: 16543.
D) Manifold shall be of Mild steel section with PP coating and Inner material shall be of SS 304.
E) Recommended operating pressure:10 Bars. 6. The capacity of hot water tank shall be minimum 1.5 times the rated capacity system. Inner Material shall be Stainless Steel SS 316 b) as per IS 1730 grade SS304-2B (22SWG). The hot water tank shall be insulated with high density injected PUF insulation 50 mm thickness between inner and outer tank. Tank stand shall be of mild steel and shall be design to withstand wind velocity of 100km/hours (minimum) or more as per site.
F) Suitable nos. ISI Marked electrical heaters along control panel, with suitable breaker, all protections, and all safety provisions so as to achieve 60 0C temperature rise in an hour. The range of thermostat shall be upto 80 0C
16.13.1 | 100 litre/ day | Set | 35255 | 2222
16.13.2 | 200 litre/ day | Set | 57059 | 3333
16.13.3 | 300 litre/ day | Set | 77299 | 4999.5
16.13.4 | 500 litre/ day | Set | 112622 | 6666
16.14 | Supply, Installation, Testing & Commissioning of Flat Plate collector (FPC) Solar Water Heating System comprising of solar flat plate collector ISI Marked made of copper sheet/copper tube, absorber toughened glass cover and aluminium extruded channel confirm to IS: 12933 (Part 1,2,3&5). The system shall have temperature gauges, strainer, water meter 2 nos., cold and hot water tank. The system shall have suitable electric backup complete with control and power wiring etc. with specification as per A, B, C, D & E
A) Cover plate: cover plate shall be toughened glass and thickness of 4.0 mm (min) conforming to section -1 of IS: 12933(pt-2)/2003 the solar transmittances of the cover plate shall be minimum 82 percent at near normal incidence.
B) Collector box: collector box shall be made of aluminium sections. The type grade, size, and finish of the material used shall be as per section-2 of IS: 12933 (pt-2)/2003: the minimum thickness of aluminium shall be as under: a. Channel section for sides 1.6 mm. b. Sheet for bottom 0.7 mm c. Support for glass retaining 1.2 mm d. Sheet for entire body 1.0 mm. The insulation of collector box shall be minimum 0.96 sq.m 0C/W for back insulation and minimum 0.48 m square degree c/w for side insulation conform to sec. 4 of IS 12933 (Part – 2) / 2003. (b) Gaskets and grommets: gaskets and grommets shall conform to Sec. 5 of IS 12933 (pt-2)/2003.
C) Absorber Shall Consist of riser, Header and Sheet for absorber. The Diameter of header shall be 25.4 + /-0.5mm and thickness 0.71mm. The Diameter of riser shall be 12.7 + /-0.5 mm and thickness 0.56mm and made of copper only. The distance between the risers from centre to centre shall be 120mm. type grade, size , workmanship and finish of the material used shall be as per section- 3 of IS : 12933 (pt -2 ) /2003 the sheet for absorber shall be of copper sheet 34 gauge/copper tube (at least 10 nos.) 4.Riser and header assembly designed for working pressure up 245 k pa (2.5 kg/ cm square) shall be tested for leakage at a minimum hydraulic pressure of 490 k pa (5 kg/ cm square). Sheet for absorber shall be made of copper only. Type Grade, size, workmanship and finis of the material used shall be per Section -3 of IS: 12933 (pt -2) /2003. 5.HDPE/LDPE cold water tank and hot water tank shall be dully erected on MS angle /channel duly painted with dual coats of enamel paint. The overall structure of solar collector plate module shall be design to with stand wind velocity of 100 kms /hr (minimum) or more as per site.
D) Hot water tank : The tank capacity shall be minimum 1.25 time the rated capacity of system. Inner tank material shall be stainless steel SS 316, as per IS 1730 GRADE SS304-2B. Hot water shall be insulated with high density injected PUF insulation: 50 mm, of 50 mm thickness between inner and outer tank ensures maximum heat rotenone ever season.
E) Suitable nos. ISI Marked electrical heaters along control panel, suitable breaker all protections, and all safety provisions so as to achieve 600C temperature rise in an hour. The range of thermostat shall be upto 800C.
16.14.1 | 100 litre/ day | Set | 38372 | 2222
16.14.2 | 200 litre/ day | Set | 61920 | 3333
16.14.4 | 300 litre/ day | Set | 86399 | 5000
16.14.5 | 500 litre/ day | Set | 123218 | 6666
16.15 | Supplying, installation , testing & commissioning of Heat pumps system for hot water using heat energy source from ambient air to Hot water, of High efficiency and energy saving operation, capable of heating water at 550 to 600 C with silent operation (the sound level should not exceed 65 dB). The Heat Pump shall have LCD display control panel with built in diagnostic and troubleshooting information and an inbuilt cycle for defrosting in case icing occurs on evaporator including all other mounting, fitting and controls, all interconnecting wiring/cabling between heat pump and electric panel etc including hot water storage tank complete in all respect with but not limited to following specifications. Power Supply V/Ph/Hz : 400V~440V, three Phase, 50Hz. Suggested Maximum output water temperature in 0C: >55 0C, ambient temperature range in 0C: -5 0C~45 0C , Type of Fan : Low Noise axial fan , Suggested Noise level: dB <65 , COP: 3.0 to 4.0. Hot Water Storage Tank consisting of GI/MS/SS cylindrical shape clarifier tank. (inlet temperature of hot water storage tank >550C) suitable for minimum 4 Kg /Sq.cm working pressure. Tank shall be provided with water flow meter, inlet / outlet, overflow, drain connection with cover, 6 mm thick tank, pressure relief valves, pressure gauge at inlet / outlet with isolation cock, thermometer at inlet / outlet, ball Valve, safety valve,check valve etc and capacity of the tank shall be for 03 Hr rated output. The complete system to be tested to a pressure of 10 Kg/cm2 complete in all respects including temperature indicators, thermostat and other required accessories. Tank shall be insulated with 100 mm thick crown 150 grade & 50 mm rock wool pads of approved quality and cladded with 24 SWG aluminium sheet cladding.
16.15.1 | 200 Litre | Set | 100157 | 6666
16.15.2 | 300 Litre | Set | 131049 | 8888
16.15.3 | 500 Litre | Set | 174272 | 12221
Note:
1 | If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## ch 17 Indoor Lighting
Chapter E - 17
Indoor Luminaires
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
17.1 | SITC of IP20 SMD Mid Power LED batten type integrated light fixture made from Powder coated Extruded aluminium housing with in built driver , System lumen efficacy ≥ 110 lm/Watt output only at CW (5700K to 6500K) , internal surge protection of 4.0 KV with Short & Open circuit protection ,THD < 10% , P. F.≥0.95, CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.1.1 | 1170mm(+/-10%) LED batten with min. lumen output 2200 lm | Each | 396 | 56
17.1.2 | 570mm (+/-10%) batten with min. lumen output 1000 lm | Each | 322 | 56
17.1.3 | 1170mm(+/-10%) LED batten with min. lumen output 4400 lm | Each | 690 | 56
17.2 | SITC of IP20 SMD Mid Power LED batten with integrated box (min.1200mmx40mmx60mm including reflector) with replacable driver fixture made from Powder coated Extruded aluminium housing ,Min. lumen output 4800 lm, System lumen efficacy ≥ 120 lm/Watt output nly at CW (5700K to 6500K), internal surge protection of 4.0 KV with Short & Open circuit protection,THD < 10% , P. F.≥0.95, CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required. | Each | 1472 | 56
17.3 | SITC of IP-20 LED Recessed / Surface Mounted, Round / Square backlit & SMD Mid Power LED Downlight with power coated die-cast aluminum housing with UV Stabilized non yellowish Diffuser with BIS compliance 4.0 KV surge protected Isolated driver, with Short & Open circuit protection input 320VAC-48 hr protection, input 350VAC-2 hr protection), having efficiency > 85% . System Lumen efficacy of ≥ 110 lm / watt,at CW (5700K to 6500K) , THD < 10 % , Pf.≥0.95, CRI >80, life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K/ 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.3.1 | Recessed Mounting
17.3.1.1 | Minimum lumen output 600 lm (lumen efficacy ≥ 100 lm / watt) | Each | 566 | 56
17.3.1.2 | Minimum lumen output 1300 lm | Each | 815 | 56
17.3.1.3 | Minimum lumen output 1600 lm | Each | 932 | 56
17.3.1.4 | Minimum lumen output 1950 lm | Each | 1098 | 56
17.3.1.5 | Minimum lumen output 2400 lm | Each | 1328 | 56
17.3.2 | Surface Mounting (with extruded alumn. Housing )
17.3.2.1 | Minimum lumen output 600 lm (lumen efficacy ≥ 100 lm / watt) | Each | 663 | 56
17.3.2.2 | Minimum lumen output 1300 lm | Each | 909 | 56
17.3.2.3 | Minimum lumen output 1600 lm | Each | 1002 | 56
17.3.2.4 | Minimum lumen output 1950 lm | Each | 1211 | 56
17.3.2.5 | Minimum lumen output 2400 lm | Each | 1464 | 56
17.4 | SITC of IP20, 2'x2' LED Surface/ Recessed mounting backlit & SMD Mid power type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmissivity UV stabilized Non -yellowish diffuser for uniform light distribution. operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V . High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection ( input 320VAC-48 hoursprotection,input 350VAC-2 hours protection) (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.4.1 | Recessed Mounting
17.4.1.1 | Minimum lumen output 4320 lm | Each | 2019 | 56
17.4.1.2 | Minimum lumen output 4800 lm | Each | 2265 | 56
17.4.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.4.2.1 | Minimum lumen output 4320 lm | Each | 2334 | 83
17.4.2.2 | Minimum lumen output 4800 lm | Each | 2599 | 83
17.5 | SITC of IP20, 1'X1' LED Surface/ Recessed mounting backlit & SMD Mid power type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmisivity UV stabilized Non -yellowish diffuser for uniform light distribution.operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.5.1 | Recessed Mounting
17.5.1.1 | Minimum lumen output 2880 lm | Each | 1302 | 56
17.5.1.2 | Minimum lumen output 3600 lm | Each | 1415 | 56
17.5.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.5.2.1 | Minimum lumen output 2880 lm | Each | 1359 | 56
17.5.2.2 | Minimum lumen output 3600 lm | Each | 1472 | 56
17.6 | SITC of IP20, 1'x4' LED Surface/ Recessed mounting Mid power SMD type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmisivity UV stabilized Non -yellowish diffuser for uniform light distribution. operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V. High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.6.1 | Recessed Mounting
17.6.1.1 | Minimum lumen output 4320 lm | Each | 1982 | 56
17.6.1.2 | Minimum lumen output 4800 lm | Each | 2152 | 56
17.6.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.6.2.1 | Minimum lumen output 4320 lm | Each | 2039 | 56
17.6.2.2 | Minimum lumen output 4800 lm | Each | 22009 | 56
17.7 | SITC of IP20, 1100-1200 mm x 50-60 mm x 70-85 mm size Suspended mounting backlit & SMD mid power type LED linear Light fixture made from Extruded Aluminium housing, PMMA Acrylic/Extruded Polycarbonate push fit type diffuser for uniform light distribution. High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection (Integral with light fixture). Lumen Efficacy will be >=100lm/W only at CW (5700K to 6500K) ,THD < 10 % , p.f.≥0.95,CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) , maximum power consumption should not more than the specified rating . Luminiare can connect each other through jointer kit (cost of jointer kit is included) as required.
17.7.1 | Minimum lumen output 2000 lm | Each | 3681 | 111
17.7.2 | Minimum lumen output 3000 lm | Each | 4361 | 111
17.8 | SITC of IP65 IK08 rated Integrated High power LED ( each LED between 3 to 5 watt power with secondary lencs on each LED) Highbay light fixture made from Pressure Die Cast Aluminium housing, UV stabilized PC Cover/ Toughened glass diffuser, potted driver, Eye bolt for mounting, system lumen efficacy ≥150 lm/Watt output , THD < 10% ,p.f.≥0.95,CRI >70 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) , maximum power consumption should not more than the specified rating and . surge protection 4 KV inbuilt & 10 KV external inside fixture as required.
17.8.1 | Minimum lumen output 12000 lm | Each | 5454 | 167
17.8.2 | Minimum lumen output 15000 lm | Each | 5946 | 167
17.8.3 | Minimum lumen output 18000 lm | Each | 7230 | 167
17.8.4 | Minimum lumen output 22500 lm | Each | 8043 | 167
17.9 | SITC of Suspended mounting IP66 IK08 rated Integrated High power LED Wellglass light fixture made from Pressure Die Cast Aluminium housing, potted driver, Eye bolt for mounting, PC clear / Opal Diffuser, system lumen efficacy ≥130 lm/Watt output only at CW (5700K to 6500K) , THD < 10% ,p.f.≥0.95,CRI >70 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) , maximum power consumption should not more than the specified rating surge protection 4 KV inbuilt & 10 KV external inside fixture as required.
17.9.1 | Minimum lumen output 4550 lm | Each | 2093 | 167
17.9.2 | Minimum lumen output 9100 lm | Each | 2787 | 167
17.1 | SITC of energy efficient /energy saving IP 20 LED direct retrofit Bulb in existing holder or fixture as required with system lumen efficacy ≥100 lm/Watt output ,pf 0.95 , CRI >70, minimum life time of minimum 25000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.10.1 | 2/3 Watt | Each | 82.5 | 11
17.10.2 | 6/7 Watt | Each | 84.8 | 11
17.10.3 | 9 Watt | Each | 96.1 | 11
17.10.4 | 15 Watt | Each | 119 | 11
17.10.5 | 18/20 Watt | Each | 145 | 11
17.11 | SITC of IP 20 box made out from 1.0 mm thick CRCA sheet steel with depth of minimun 30 mm and finished with powder coating and suitable for mounting LED tube including side covers, holders , internal wiring to illuminate the single sided connection LED tube. ( Without tube).
17.11.1 | Suitable for 2' LED Tube shape fixture for single rod | Each | 158 | 11
17.11.2 | Suitable for 4' LED Tube shape fixture for single rod | Each | 249 | 11
17.11.3 | Suitable for 4' LED Tube shape fixture for double rod | Each | 317 | 11
17.12 | SITC of energy efficient direct fit (Retrofit) Polycarbonate/ Glass housing SMD Mid Power LED tube rod (with integral driver & alumn. heat sink ), on existing fixture. system lumen efficacy ≥ 100 lm/Watt outputonly at CW (5700K to 6500K) , internal surge protection of 2.5 KV,THD < 15% ,p.f.≥0.95,CRI >80 , life time of minimum 35000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.12.1 | 600mm , Min. Lumens output 1800 lm LED Tube rod with Polycarbonate Housing | Each | 215 | 11
17.12.2 | 1200mm , Min. Lumens output 2000 lm LED Tube rod with Polycarbonate Housing | Each | 260 | 11
17.12.3 | 1200mm, Min. Lumens output 2000 lm LED Tube rod with Glass Housing | Each | 238 | 11
17.13 | SITC of IP65 IK08 rated Integrated SMD Mid power LED bulk head type light fixture made from Pressure Die Cast AL housing suitable with integral driver, system lumen efficacy ≥120 lm/Watt output only at CW (5700K to 6500K) , THD < 15% ,p.f.≥0.95,CRI >80 , life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.13.1 | Minimum lumen output 1200 lm | Each | 1386 | 111
17.14 | SITC of IP-20 LED Recessed / Surface Mounted, Round / Sqaure backlit & SMD Mid Power LED Downlight with power coated die-cast aluminum housing with UV Stabilized non yellowish Diffuser with BIS complience 4.0 KV surge protected Isolated driver, with Short & Open circuit protection input 320VAC-48 hr protection, input 350VAC-2 hr protection), having efficiency > 85% . System Lumen efficacy of ≥ 110 lm / watt,at CW (5700K to 6500K) , THD < 10 % , Pf.≥0.95, CRI >80, UGR (unified glare rating)<19, fliker free (current ripple should be below 5%), SDCm (standard deviation colour matching)<5.life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K/ 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.14.1 | Recessed Mounting
17.14.1.1 | Minimum lumen output 1300 lm | Each | 1119 | 56
17.14.1.2 | Minimum lumen output 1600 lm | Each | 1279 | 56
17.14.1.3 | Minimum lumen output 1950 lm | Each | 1515 | 56
17.14.1.4 | Minimum lumen output 2400 lm | Each | 1835 | 56
17.14.2 | Surface Mounting (with extruded alumn. Housing )
17.14.2.1 | Minimum lumen output 1300 lm | Each | 1234 | 56
17.14.2.2. | Minimum lumen output 1600 lm | Each | 1364 | 56
17.14.2.3 | Minimum lumen output 1950 lm | Each | 1772 | 56
17.14.2.4 | Minimum lumen output 2400 lm | Each | 2067 | 56
17.15 | SITC of IP20, 2'x2' LED Surface/ Recessed mounting backlit & SMD Mid power type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmisivity UV stabilized Non -yellowish diffuser for uniform light distribution. operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V . High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection ( input 320VAC-48 hoursprotection,input 350VAC-2 hours protection) (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , UGR (unified glare rating)<19, fliker free (current ripple should be below 5%), SDCm (standard deviation colour matching)<5 life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.15.1 | Recessed Mounting
17.15.1.1 | Minimum lumen output 4320 lm | Each | 2719 | 56
17.15.1.2 | Minimum lumen output 4800 lm | Each | 3229 | 56
17.15.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.15.2.1 | Minimum lumen output 4320 lm | Each | 2939 | 83
17.15.2.2 | Minimum lumen output 4800 lm | Each | 3449 | 83
17.16 | SITC of IP20, 1'x4' LED Surface/ Recessed mounting Mid power SMD type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmisivity UV stabilized Non -yellowish diffuser for uniform light distribution. operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V. High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , UGR (unified glare rating)<19, fliker free (current ripple should be below 5%), SDCM (standard deviation colour matching)<5life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.16.1 | Recessed Mounting
17.16.1.1 | Minimum lumen output 4320 lm | Each | 2889 | 56
17.16.1.2 | Minimum lumen output 4800 lm | Each | 3115 | 56
17.16.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.16.2.1 | Minimum lumen output 4320 lm | Each | 3059 | 56
17.16.2.2 | Minimum lumen output 4800 lm | Each | 3285 | 56
17.17 | SITC of IP20, 1'X1' LED Surface/ Recessed mounting backlit & SMD Mid power type LED Light fixture not less than 35 mm housing depth made from CRCA sheet steel housing, high purity / transmisivity UV stabilized Non -yellowish diffuser for uniform light distribution.operating voltage range 140-285 V, HV cutoff - LV cutoff should be 300-100V High efficiency with 4 KV internal surge protection BIS certified isolated driver having efficiency > 85% , with Short & Open circuit protection (Integral with light fixture). System lumen efficacy of ≥ 120 lm/Watt ,THD < 10 % , p.f.≥0.95,CRI >80 , UGR (unified glare rating)<19, fliker free (current ripple should be below 5%), SDCM (standard deviation colour matching)<5 life time of minimum 50000 Burning Hours with , 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.17.1 | Recessed Mounting
17.17.1.1 | Minimum lumen output 2880 lm | Each | 1642 | 56
17.17.1.2 | Minimum lumen output 3600 lm | Each | 1840 | 56
17.17.2 | Surface Mounting (Driver should be Inside the Luminaire)
17.17.2.1 | Minimum lumen output 2880 lm | Each | 1812 | 56
17.17.2.2 | Minimum lumen output 3600 lm | Each | 1959 | 56
17.18 | SITC of IP-20 LED Recessed Mounted, Round backlit & COB type LED Downlighter of Powder Coated diecast/Extruded Aluminium body including trim with aluminium deflector and construction as per IS:10322 with 2.5 KV surge protected Isolated driver with Short & Open circuit protection (Input 320VAC-48 hours protection, Input 350VAC-2 hours protection) having efficiency > 85%, operating voltage 140-270 V AC. System Lumen efficacy of ≥ 100 lm /watt, at CW (5700K to 6500K) , THD < 10 % , Pf.≥0.95, CRI >80, UGR(Unified Glare Rating)< 19, Fliker free(current ripple should be below 5%), SDCM(Standard Deviation Color Matching) < 5, life time of minimum 50000 Burning Hours with 70% of intial Lumen maintaned till life ends , CCT 3000°K / 4000°K/ 5700°K /6000°K/6500°K (As per ANSI Bin) as required.
17.18.1 | lumen output 550 lm to 770 lm | Each | 792 | 56
17.18.2 | lumen output 880 lm to 1100 lm | Each | 1132 | 56
17.18.3 | lumen output 1320 lm to 1650 lm | Each | 1415 | 56
Note:
To ensure technical compliance of LED luminaries :
1. The fixture shall confirm to relevant BIS standards and bear trade mark certificate from the Manufacturer. Manufacturers Word Mark and it's Name should be Engraved/ Embossed or Screen printed on the housing. Product lable should display the system lumens Information along with the wattage.
2. The OEM must ensure that their products are tested for compliance, through their in house laboratory equipped with "C" type photogonio meter and accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and test methods specified in BIS 10322 for Led luminaires.
3. OEM shall provide LM-80 reports based on the methods developed by IES (Illumination Engineering Society). Heat Sink of aluminium housing should be such that LED junction temperature shall not rise above 90 degree C.
4. If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## ch 18Outdoor Luminaires & Poles
Chapter E - 18
Outdoor Luminaires & Poles
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
18.1 | Supply and erection of Galvanized Iron pole with galvanizing done in single dipping (Average coating thickness Minimum 65 Microns) continuously tapered poles having Octagonal / Circular/ Conical cross-sections designed to withstand the maximum wind speed as per IS 875, The pole shaft shall be made from sheet steel (HT Steel Conforming to grade S355JO) and confirming to BSEN 10025 and shall be continuously tapered with single longitudinal welding. There shall not be any circumferential welding. The welding of pole shaft shall be done by Submerged Arc Welding (SAW) process. pole shafts shall be provided with the rigid flange plate of suitable thickness (Fe 410 conforming to IS 226 / IS 2062) with provision for fixing 4 no. foundation bolts, The base plate shall be fillet welded to the pole shaft at two locations i.e. from inside and outside.The octagonal Poles shall have hinged lockable door of approximate 500 mm length at the elevation of 500 mm from the Base plate with bakelite sheet having 6A SP MCB and 16 sqmm stud type connector ( 4 nos) inside the pole at door opening for cable connection of following length and dimension as per table P-01 for Octagonal & P-02 for Conical with base plate and foundation bolt on the Existing cement concrete foundation. To ensure quality of product it's entire manufacturing process starting from sheet cutting to galvanization sould be done under one premises.
18.1.1 | Poles with Octagonal/Conical Cross Section
18.1.1.1 | 3 Mtr. | Each | 5308 | 253
18.1.1.2 | 4 Mtr. | Each | 6414 | 305
18.1.1.3 | 5 Mtr. | Each | 7757 | 369
18.1.1.4 | 6 Mtr. | Each | 9449 | 450
18.1.1.5 | 7 Mtr. | Each | 10741 | 512
18.1.1.6 | 8 Mtr. | Each | 12838 | 611
18.1.1.7 | 9 Mtr. | Each | 16085 | 766
18.1.1.8 | 10 Mtr. | Each | 18819 | 896
18.1.1.9 | 11 Mtr. | Each | 24151 | 1150
18.1.1.10 | 12 Mtr. | Each | 30293 | 1443
18.2 | Supply and Fixing of Pole OEM fabricated hot dipped galvanised M.S. Overhang (48.3 X 3.25 mm) with cap ( 250x 88.9 / 114.3 x 3.25 mm) over the existing poles.
18.2.1 | Single arm overhang | Mtr. | 1504 | 72
18.2.2 | Double arm overhang | Mtr. | 2358 | 112
18.3 | Supply and erection of Galvanized Iron pole with galvanizing done in single dipping (Average coating thickness Minimum 65 Microns) Swaged tubular pole conforming to IS: 2713-1980 (part I to II) with galvanised base plate, The pole shall be made from steel tube & Pipe (IS:1141, Fe 410) including excavation of the pit and filling the same with C.C. of M-20 grade (1:1.5:3) from base plate to 50 cm above ground level, with the help of steel frame not less than 40 cm dia up to 114.3mm outer dia and 50 cm beyond 114.3mm outer dia around the pole. Duly finished with cement plaster, earthing terminals, cable entry with 32 mm dia. 'B' class GI cable sleeves complete as required. of following height & designation. ( See Table P - 03 for specs. )
18.3.1 | 7.5 Mtr. ( 410 SP - 5 ) | Each | 13425 | 1438
18.3.2 | 8.5 Mtr. ( 410 SP - 17 ) | Each | 14821 | 1588
18.3.3 | 9.0 Mtr. ( 410 SP - 28 ) | Each | 18172 | 1947
18.3.4 | 10 Mtr. ( 410 SP - 42 ) | Each | 23871 | 2558
18.3.5 | 11 Mtr. ( 410 SP - 51 ) | Each | 26664 | 2857
18.3.6 | 12 Mtr. ( 410 SP - 59 ) | Each | 32806 | 3515
18.4 | Add for supply and fixing of Pole OEM fabricated Galvanized Overhang of following size over the existing poles.
18.4.1 | 76.1 mm OD x 3.25 mm thickness | Mtr. | 1487 | 71
18.4.2 | 88.9 mm OD x 3.25 mm thickness | Mtr. | 1844 | 88
18.4.3 | 114.3 mm OD x 3.65 mm thickness | Mtr. | 2499 | 119
18.5 | Supply and erection of Mild steel Swaged tubular pole conforming to IS: 2713-1980 (part I to II) with base plate, The pole shall be made from steel tube & Pipe (IS:1141, Fe 410) including excavation of the pit and filling the same with C.C. of M-20 grade (1:1.5:3) from base plate to 50 cm above ground level, with the help of steel frame not less than 40 cm dia up to 114.3mm outer dia and 50 cm beyond 114.3mm outer dia around the pole. Duly finished with cement plaster, earthing terminals, cable entry with 32 mm dia. 'B' class GI cable sleeves. After erection pole shall be painted with two coat of red oxide primer and two coat of enamel paint of silver colour as per the direction of Engineer incharge complete as required of following height & designation. ( See Table P - 03 for specs. )
18.5.1 | 7.5 Mtr. ( 410 SP - 5 ) | Each | 10806 | 1158
18.5.2 | 8.5 Mtr. ( 410 SP - 17 ) | Each | 11885 | 1273
18.5.3 | 9.0 Mtr. ( 410 SP - 28 ) | Each | 14474 | 1551
18.5.4 | 10 Mtr. ( 410 SP - 42 ) | Each | 19023 | 2038
18.5.5 | 11 Mtr. ( 410 SP - 51 ) | Each | 21181 | 2269
18.5.6 | 12 Mtr. ( 410 SP - 59 ) | Each | 25927 | 2778
18.6 | Add for supply and fixing of Pole OEM fabricated Mild steel Overhang of following size over the existing poles, Overhang shall be painted with two coat of red oxide primer and two coat of enamel paint of silver colour as required.
18.6.1 | 76.1 mm OD x 3.25 mm thickness | Mtr. | 1166 | 56
18.6.2 | 88.9 mm OD x 3.25 mm thickness | Mtr. | 1487 | 71
18.6.3 | 114.3 mm OD x 3.65 mm thickness | Mtr. | 2047 | 97
18.7 | Supply installation testing & Commissioning of high mast lighting system (as per PLG 07 of ILP UK techinical report no 7 of ILE UK /IS:875 Part-1 – 2015//BSEN10025/and IS:2062 )consisting of totally hot dip galvanised by piecewise single dipped method high mast, lantern carriage suitable for up to 18 nos luminaries with welded arm (excluding luminares), mast head frame assembly with full cover, including 1 No. LED 15 Watts aviation obstruction light, double drum type self sustaining winch, integral power tool accessible from door with padlocking arrangement (winch motor with control circuit) hot dipped galvanised heavy duty pipe lightening finial, Stainless steel 6 mm dia. wire ropes (AISI 316, 7 / 19 costruction 3 no. rope for lantern carrage & 2 no. rope for winch assembly ) foundation bolt, torque limiter,EPR insulated PCP sheathed 5 core x 2.5 Sq.mm trailing cable, including outdoor type control panel for auto on / off, reverse / forward motor operation. The mast is constructed from mild steel plates (as per IS 5986 Gr. 510 ) cut and folded to form a polygonal section, telescopic jointed and welding as per BS 5135.etc. as required including cost of RCC Foundation as per OEM Design & Drawings . ( See table P - 04 for specs.) To ensure quality of the product, OEM Must have Type test certificate for wind tunnel test from IIT. Entire manufacturing process starting from sheet cutting to galvanization should be done under one premises Inhouse galvanizing plant shall have bath length not less then 12.0 mtr to ensure the quality of galvanization .
18.7.1 | 12.5 Mtr HM (in 2 section) suitable for 6 No. Luminaries 2 no. rope for lantern carrage & 2 no. rope for winch assembly | Each | 179651 | 8555
18.7.2 | 16.0 Mtr HM (in 2 section) | Each | 239521 | 11406
18.7.3 | 20.0 Mtr Hm (in 2 section) | Each | 284198 | 13533
18.7.4 | 25.0 Mtr HM (in 3 section) | Each | 375711 | 17891
18.7.5 | 30.0 Mtr HM (in 3 section) | Each | 450452 | 21450
18.8 | Providing and Laying RCC Foundation for Octagonal / Conical Street Light poles as per Drawing attach at Table P-05 with Following Procedure
A) Excavation of Pit for Foundation Size upto required depth from Ground level
B) Dressing of Pit and Dry stone pitching 200 mm thick including supply of stones and preparing surface complete.
C) Providing and laying in position cement concrete of M-10 grade of 75 mm thickness
D) Reinforcement for R.C.C. work with TMT bars including straightening, cutting, bending, placing in position and binding all complete.
E) Centring and shuttering including strutting , propping etc. and removal of form work for Footing and Pedestal
F) Providing & Fixing of 2 no. Required Size PLB HDPE Pipe & Foundation Bolt with template as per OEM Recommendations.
G) Providing and Laying Reinforce cement Concrete of M-20 grade in Footing and Pedestal including Curing the foundation for minimum 7 days.
H) Providing and Fixing Nosing Angle 25 mm x 25 mm x 3mm with 2 no. of 100 mm long, 6 mm dia fastener
18.8.1 | Pole Foundation for Octagonal pole from 3 Mtr. To 6 Mtr. |  | 3449 | 889
18.8.2 | Pole Foundation for Octagonal pole from 7 Mtr. To 9 Mtr. |  | 4959 | 1111
18.8.3 | Pole Foundation for Octagonal pole from 10 Mtr. To 12 Mtr. |  | 7389 | 1333
18.9 | Providing & Fixing of IP-65 Protected LED aviation obstruction light luminaire comprising of die cast aluminium alloy housingwith Polycarbonate enclosure having more than 200 No's Low Power LED's having minimum power consumption 15 watts complete in all respect.
18.9.1 | aviation obstruction LED light luminaire 12/15 Watts | Each | 3827 | 182
18.10 | Providing & Fixing of IK07 IP65 protected Top/Bottom mounted LED Post top Luminarie top & bottom made of single piece construction powder coated die cast alluminium housing with UV stabalized Clear / frosted Polycarbonate diffuser and Aluminium anodised with powder quoted reflector. The System level Luminous efficacy ≥ 80 Lumen/W. SMD LEDs is to be used, System CRI>70, CCT: 3000/4000/6500 K. The integral electronic driver must be potted & has a unique BIS R number constant current and Internal/external surge protection device of min. 4KV(L-N) and efficiency > 85%, PF>0.9, THD<10% and input Voltage range of 140-270V AC at 50Hz. System life of 50000 Burning hours with 70% of Initial Lumens maintained . LED Driving output current <750mA as required.
18.10.1 | Minimum lumen output 2800 lm Post top Luminarie | Each | 4697 | 278
18.10.2 | Minimum lumen output 3200 lm Post top Luminarie | Each | 5377 | 278
18.10.3 | Minimum lumen output 3600 lm Post top Luminarie | Each | 6340 | 278
18.11 | Providing & Fixing of IK08 IP-66 protected high power LED flood light system with single piece Pressure diecast aluminium housing, toughened glass with suitable lenses on LED / integrated lens diffuser to achieve various beam angles, of high power LED of 3 to 5 watt each . Integrated metal case potted driver as a unique BIS R number (as per IS 15885) having efficiency more than 85 % and in compliance to BIS certified and Trade mark certificate(Fitting & driver both have separate BIS R number). The System level Luminaire efficacy >=130 lm/ wt. LED driver Input Voltage AC 120 to 270 V AC with High voltage Cutoff @>=300 V AC & Low Voltage cutoff @>=90 V AC and Auto resetting Safety .Power Factor >0.95 , THD(I) <10% , LED driving output current <=750mA. driver should be Phase to phase protection of 440 V for 4 Hrs. Electrical Connector , Surge Protection Min >=4KV internal and 10KV external but inside driver compartment, System life of 50000 Burning hours with 70% of Initial Lumens maintained, CRI>70 and CCT 5700K ±355K as required.
18.11.1 | High Power LED Flood Light Minimum lumen outpu 3900 lm | Each | 2131 | 102
18.11.2 | High Power LED Flood Light Minimum lumen output 6500 lm | Each | 2631 | 126
18.11.3 | High Power LED Flood Light Minimum lumen output 10400 lm | Each | 3603 | 172
18.11.4 | High Power LED Flood Light Minimum lumen output 13000 lm | Each | 3689 | 176
18.11.5 | High Power LED Flood Light Minimum lumen output 15600 lm | Each | 4760 | 227
18.11.6 | High Power LED Flood Light Minimum lumen output 19500 lm | Each | 5949 | 283
18.11.7 | High Power LED Flood Light Minimum lumen output 23400 lm | Each | 7258 | 346
18.11.8 | High Power LED Flood Light Minimum lumen output 26000lm | Each | 8924 | 425
18.11.9 | High Power LED Flood Light Minimum lumen output 32500 lm | Each | 9519 | 453
18.11.10 | High Power LED Flood Light Minimum lumen output 39000 lm | Each | 11899 | 567
18.11.11 | High Power LED Flood Light Minimum lumen output 45500 lm | Each | 16063 | 765
18.11.12 | High Power LED Flood Light Minimum lumen output 52000 lm | Each | 19242 | 916
18.11.13 | High Power LED Flood Light Minimum lumen output 65000 lm | Each | 22013 | 1048
18.12 | Providing & Fixing of IK08, IP 66 protected LED Street Light Luminaire on existing bracket/pole. Fixture made of powder coated single piece pressure die cast aluminum material with heat dissipation fins on housing and secondary lens on each LED/ integrated lens diffuser without cover & should be High power LED of 3 to 5 watt each . The System efficacy >=135 lm/ wt and integrated metal case potted driver & has a unique BIS R number ( as per IS 15885) with Input Voltage AC 120 to 270 V AC with High voltage Cutoff @>=300 V AC & Low Voltage cutoff @>=90 V AC and Auto resetting Safety , Power Factor >0.95 driver Efficiency >85% ,THD(I) <10% Humidity 10% to 90% RH Working Temp -5C to 45C . LED driving output current <750mA. The luminaire shall be BIS certified (Fitting & driver both have separte BIS R number) and Trade mark certified. Life Expectancy Equal or more than 50000 burning hrs with Minimum 70% lumen maintened , CRI >70 and CCT 5700K +355K. Surge protection shall be min ≥ 4 KV internal and min 10 KV external inside driver compartment. driver should be Phase to phase protection of 440 V for 4 Hrs as required.
18.12.1 | LED Street Light fixture with Minimum lumen output 2700 lm | Each | 1666 | 76
18.12.2 | LED Street Light fixture with Minimum lumen output 4050 lm | Each | 1785 | 85
18.12.3 | LED Street Light fixture with Minimum lumen output 6075 lm | Each | 2677 | 128
18.12.4 | LED Street Light fixture with Minimum lumen output 8100 lm | Each | 3004 | 143
18.12.5 | LED Street Light fixture with Minimum lumen output 9450 lm | Each | 3570 | 170
18.12.6 | LED Street Light fixture with Minimum lumen output 12150 lm | Each | 4641 | 221
18.12.7 | LED Street Light fixture with Minimum lumen output 13500 lm | Each | 5236 | 249
18.12.8 | LED Street Light fixture with Minimum lumen output 16200 lm | Each | 5949 | 283
18.12.9 | LED Street Light fixture with Minimum lumen output 20250 lm | Each | 7853 | 374
18.12.10 | LED Street Light fixture with Minimum lumen output 24300 lm | Each | 8567 | 408
18.12.11 | LED Street Light fixture with Minimum lumen output 28350 lm | Each | 9995 | 476
18.13 | Providing & Fixing of IK08, IP 66 protected LED Street Light Luminaire on existing bracket/pole. Fixture made of powder coated single piece pressure die cast aluminum material with heat dissipation fins on housing with UV stabilized PC (UV stablization report submitted for UV cover ) /Toughened Glass cover and secondary lens on each LED/ integrated lens diffuser & should be High power LED of 3 to 5 watt each . The System efficacy >=125 lm/ wt and integrated metal case potted driver & has a unique BIS R number ( as per IS 15885) with Input Voltage AC 120 to 270 V AC with High voltage Cutoff @>=300 V AC & Low Voltage cutoff @>=90 V AC and Auto resetting Safety , Power Factor >0.95 driver Efficiency >85% ,THD(I) <10% Humidity 10% to 90% RH Working Temp -5C to 45C . LED driving output current <750mA. The luminaire shall be BIS certified (Fitting & driver both have separte BIS R number) and Trade mark certified. Life Expectancy Equal or more than 50000 burning hrs with Minimum 70% lumen maintened , CRI >70 and CCT 5700K +355K. Surge protection shall be min ≥ 4 KV internal and min 10 KV external inside driver compartment. driver should be Phase to phase protection of 440 V for 4 Hrs as required.
18.13.1 | LED Street Light fixture with Minimum lumen output 2500 lm | Each | 1725 | 82
18.13.2 | LED Street Light fixture with Minimum lumen output 3750 lm | Each | 1844 | 88
18.13.3 | LED Street Light fixture with Minimum lumen output 5625 lm | Each | 2767 | 132
18.13.4 | LED Street Light fixture with Minimum lumen output 7500 lm | Each | 3123 | 149
18.13.5 | LED Street Light fixture with Minimum lumen output 8750 lm | Each | 3689 | 176
18.13.6 | LED Street Light fixture with Minimum lumen output 11250 lm | Each | 4760 | 227
18.13.7 | LED Street Light fixture with Minimum lumen output 12500 lm | Each | 5474 | 261
18.13.8 | LED Street Light fixture with Minimum lumen output 15000 lm | Each | 6068 | 289
18.13.9 | LED Street Light fixture with Minimum lumen output 18750 lm | Each | 7913 | 377
18.13.10 | LED Street Light fixture with Minimum lumen output 22500 lm | Each | 9222 | 239
18.13.11 | LED Street Light fixture with Minimum lumen output 26250 lm | Each | 10412 | 496
18.14 | Providing & Fixing of IK08 IP65 protected 600-800 mm height LED Bollard Luminarie with base plate made of powder coated die cast aluminium housing with UV stabalized PC diffuser. The System level Luminous efficacy ≥ 80 Lumen/W. SMD LEDs is to be used, System CRI>70, CCT: 3000/4000/6500 K. The integral electronic driver must be potted & has a unique BIS R number constant current and Internal/external surge protection device of min. 4KV(L-N) and efficiency > 85%, PF>0.9, THD<20% and input Voltage range of 90-270V AC at 50Hz. System life of 30000 Burning hours with 70% of Initial Lumens maintained Light output in Cool white or Warm White Colour as per engineers choice. LED driving output current <750mA. as required.
18.14.1 | Minimum lumen output 800 lm Bollard | Each | 6544 | 312
18.14.2 | Minimum lumen output 980 lm Bollard | Each | 8567 | 408
18.15 | Providing & Fixing of IK08 IP66 / IP67 protected Rectangular shape LED Step Luminarie made of powder coated die cast alluminium housing with UV stabalized PC diffuser. The System level Luminous efficacy ≥ 60 Lumen/W. SMD LEDs is to be used, System CRI>70, CCT: 3000/4000/6500 K. The integral electronic driver must be potted & has a unique BIS R number constant current and Internal/external surge protection device of min. 4KV(L-N) and efficiency > 85%, PF>0.9, THD<20% and input Voltage range of 140-270V AC at 50Hz. System life of 50000 Burning hours with 70% of Initial Lumens maintained . driver current <750mA as required.
18.15.1 | Minimum lumen output 450 lm Step light | Each | 2261 | 108
18.15.2 | Minimum lumen output 630 lm Step light | Each | 3153 | 150
18.15.3 | Minimum lumen output 800 lm Step light | Each | 3867 | 184
18.16 | Providing & Fixing of IK08 IP65 / IP66 protected LED Up - Down Luminarie Wall / Surface mounting made of powder coated die cast alluminium housing with with UV stabalized PC diffuser. The System level Luminous efficacy ≥ 80 Lumen/W. COB LEDs is to be used, System CRI>70, CCT: 3000/4000/6500 K. The integral electronic driver must be potted & has a unique BIS R number constant current and Internal/external surge protection device of min. 4KV(L-N) and efficiency > 85%, PF>0.9, THD<10% and input Voltage range of 140-270V AC at 50Hz. System life of 50000 Burning hours with 70% of Initial Lumens maintained Light output in Cool white or Warm White Colour as per engineers choice. LED driving output current <750mA. as required.
18.16.1 | Minimum lumen output 800 lm Up-Down Luminary | Each | 3332 | 159
18.16.2 | Minimum lumen output 1300 lm Up-Down Luminary | Each | 4522 | 215
18.16.3 | Minimum lumen output 2150 lm Up-Down Luminary | Each | 5355 | 255
18.17 | Providing and fixing of fuse box size 250(H) x 200(W) x 150(D) mm fabricated of 1.6mm MS sheet with hinged cover, dust and vermin proof, rubber gasket, locking arrangement, duly holded with 2 nos pole clamps of 20 mm x 3 mm flat with nut and bolts, complete with anticorrosive treatment, finished with two coat of approved enamel paint. The box shall be provided with 2 / 4 nos copper bus bar 125 x 20 x 3 mm with brass screws suitable supports,earth terminal, inter connection, knock outs for 20 / 25 mm cable gland, 1 no. 6 Amp MCB complete in all respect. | Each | 1886 | 90
18.18 | Providing and fixing of IP 65 protected Polycarbonate / Polysterene fuse box moulded with inside knock outs of following size with hinged cover, transparent window, PU gasket, locking arrangement, duly holded with 2 nos. pole clamps of 20 mm x 3 mm flat with nut and bolts, The box shall be provided with Din rail, 4 / 8 way 10.0 / 16.0 sq.mm heavy duty connector, earth terminal, complete in all respect.
18.18.1 | 125 mm X 200 mm X 122 mm | Each | 1666 | 79
18.18.2 | 160 mm X 225 mm X 100 mm | Each | 1963 | 93
18.18.3 | 200 mm X 200 mm X 122 mm | Each | 2558 | 122
18.18.4 | 225 mm X 225 mm X 100 mm | Each | 3629 | 173
18.19 | Providing & Fixing of Street light bracket made out from following size of ' B ' class , Medium class G.I. Pipe confirming to IS : 1239 P - 1 ( 2004 ) with heavy duty pole clamp, Saddles suitable fastners etc. as required.
18.19.1 | 20 mm Dia. | Mtr. | 276 | 67
18.19.2 | 25 mm Dia. | Mtr. | 384 | 89
18.19.3 | 32 mm Dia. | Mtr. | 482 | 111
18.19.4 | 40 mm Dia. | Mtr. | 558 | 133
18.2 | Providing & Fixing of IP - 65 protected impact resistant polycarbonate / Polysterene enclosures with knock out for cable entry/out including fixing with nut, bolt, fatner etc as required complete in all respect of following sizes.
18.20.1 | 180 x 180 x 91 mm | Each | 1285 | 84
18.20.2 | 250 x 200 x 115 mm | Each | 1892 | 124
18.20.3 | 300 x 450 x 132 mm | Each | 3007 | 197
18.20.4 | 320 x 440 x 179 mm | Each | 4353 | 285
18.20.5 | 320 x 640 x 179 mm | Each | 5796 | 379
18.21 | Supply and erection of PU coated , 6 to 7 mm thick Glass / Fibre Reinforced Pole (GRP /FRP) made by CNC filament winding machine using thermoset resin polyester/epoxy resin system) having minimum 62% glass content. designed to withstand the maximum wind speed as per IS 875, and Tested for deflection not more than 15% length of pole as per ASTM D 4923, The pole should be in one piece and tapered round in shape, pole shafts shall be provided with FRP Anchor with suitable MS cated Base with provision for fixing 4 no. foundation bolts( Including cost of Foundation Bolt), The Pole shall have lockable door of approximate 500 mm length at the elevation of 500 mm from the Base plate with bakelite sheet having 6A SP MCB and 16 sqmm stud type connector ( 4 nos) inside the pole at door opening for cable connection of following length and dimension on Existing cement concrete foundation .
18.21.1 | 3 Mtr. Long, Top/ Bottom OD Dia 89/126mm ± 2mm approx. With Base 250X250 X 10mm | Each | 9519 | 453
18.21.2 | 4 Mtr. Long, Top/ Bottom OD Dia 89/131mm ± 2mm approx. With Base 250X250 X 10mm | Each | 12494 | 453
18.21.3 | 5 Mtr. Long, Top/ Bottom OD Dia 89/141mm ± 2mm approx. With Base 250X250 X 10mm | Each | 14041 | 669
18.21.4 | 6 Mtr. Long, Top/ Bottom OD Dia 89/152mm ± 2mm approx. With Base 250X250 X 10mm | Each | 15706 | 748
18.21.5 | 7 Mtr. Long, Top/ Bottom OD Dia 89/157mm ± 2mm approx. With Base 300X300 X 12mm | Each | 172553 | 822
18.21.6 | 8 Mtr. Long, Top/ Bottom OD Dia 89/157mm ± 2mm approx. With Base 300X300 X 12mm | Each | 19633 | 935
18.21.7 | 9 Mtr. Long, Top/ Bottom OD Dia 89/183mm ± 2mm approx. With Base 300X300 X 12mm | Each | 22013 | 1048
18.21.8 | 10 Mtr. Long, Top/ Bottom OD Dia 89/207mm ± 2mm approx. With Base 350X350 X 15mm | Each | 25226 | 1201
18.21.9 | 11 Mtr. Long, Top/ Bottom OD Dia 89/217mm ± 2mm approx. With Base 350X350 X 15mm | Each | 27367 | 1303
18.21.10 | 12 Mtr. Long, Top/ Bottom OD Dia 89/226mm ± 2mm approx. With Base 400X400 X 20mm | Each | 33912 | 1615
18.22 | Supply, Erection and Fixing of GRP Overhang with cap over the existing poles.
18.22.1 | Single arm overhang | Mtr. | 3546 | 169
18.22.2 | Double arm overhang | Mtr. | 5057 | 241
18.23 | Supply, Installation, Testing and Commissioning of Smart Lighting Controller in existing feeder panels which includes, Inbuilt energy metering with 3 nos CT, Three phase power supply with withstanding capability up to 500 VAC, Instant mode, Fixed Mode, Astronomical Mode, Hybrid Mode, Interval Mode, Offset in Sunset and Sunrise Timing for scheduling. Provision for measurement of all three phase electrical parameters like voltage, current, power factor, power, frequency, energy with atleast class 1 accuracy and compliant with IS13779 standard, UV-OV protection, backup battery 4 hrs, Andriod/iOS app and software to operate form computer, provision to add display device externally, support for RS485 communiction , inbuilt GSM/GPRS 4G modem with 2G fallback, Real time GPS based clock, calender, lithium ion battery backup for RTC clock, Three relay output, Minimum Ninety days data memory inbuilt backup facility, Controller shall be type tested with NABL approved lab for EFT or burst testing for conducted immunity in accordance with IEC 610000-4-4, Software application should utilize a Low-Code/No-Code platform to simplify development and customization. It must be hardware-agnostic and compatible with other IoT-based smart city applications. Software should have undergone a "Vulnerability Assessment and Penetration Testing (VAPT)" as per OWASP Top 10 2021 and 2022, SANS CWE 24 & CERT-In Standard.Dedicated IoT communication GSM/GPRS SIMCard (with minimum 3 years of recharge)for 4G Communication with software application. 3 Years Data Hosting & Server Charges to be included with software. | Each | 26177 | 1247
18.24 | S&F of Architectural Facade Linear Light, LED, 24V DC, IP 66, DMX, The housing made of high strength extruded aluminium alloy 6063 grade & die-cast aluminium end caps with Electrostatically applied polyester powder coating, silicon gasket and clear tempered glass for high impact resistance, Power Supply external 24V DC.Temp range 0°C to 45°C. McAdam standard deviation for color matching (SDCM) shall be ≤ 3. CRI 80 (for white). Discrete LED Module with high efficacy LED's, on Printed Circuit Board with metal core plate. Suitable Power Supply 24V DC for LED Module, which offers Protection against Short Circuit, Over- Voltage & Over- Current, with in-built surge protection. Lens made of PMMA which should offer various type of symmetric/asymmetric optics : 15°x35°/25°x40° etc, System life L70 @50,000 hours Supporting LM80 report from LED Manufacturer should be submitted.
18.24.1 | 12W 3000K/4000K ≥80LPW,Min 960lumens luminaire length 1000mm, width 25mm & height 35mm | Each | 7734 | 368
18.24.2 | 24W 3000K/4000K ≥80LPW,Min 1920lumens luminaire length 1000mm, width 38mm & height 47mm | Each | 9519 | 453
18.24.3 | 36W 3000K/4000K ≥80LPW,Min 2880lumens luminaire length 1000mm, width 38mm & height 47mm | Each | 11899 | 567
18.25 | Providing & Fixing of IK10/ IP66 protected pole mount LED Post top Luminarie top & bottom made of single piece construction powder coated pressure die cast alluminium housing with High purity PC diffuser, downward illumination to control light pollution. The System level Luminous efficacy ≥ 120 Lumen/W. SMD LEDs is to be used, System CRI>/=70, CCT: 4000/5700 K. Driver must be potted & has a unique BIS R number constant current and Internal/external surge protection device of min. 4KV(L-N) and efficiency > 85%, PF>0.95, THD<10% and with Input Voltage AC 120 to 270 V AC with High voltage Cutoff @>=300 V AC and Auto resetting Safety, driver should be Phase to phase protection of 440 V for 4 Hrs. System life of 50000 Burning hours with 70% of Initial Lumens maintained . LED driving current <750mA. Mounting pole diameter 060mm, The Luminaire dimension min Dia 450mm x 200mm(H). including making connections etc. as required.
18.25.1 | Minimum lumen output 5000 lm Post top Luminaire | Each | 8154 | 278
18.25.2 | Minimum lumen output 6000 lm Post top Luminaire | Each | 9283 | 278
Note:
1. To ensure technical compliance of LED luminaries :
a). The fixture shall confirm to relevant BIS standards and bear trade mark certificate from the Manufacturer. Manufacturers Word Mark and it's Name should be Engraved/ Embossed or Screen printed on the housing. Product level should display the system lumens information along with the wattage.
b). The OEM must ensure that their products are tested for compliance, through their in house laboratory equipped with "C" type photogonio meter and accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and test methods specified in BIS 10322 for Led luminaires.
c). OEM shall provide LM-80 reports based on the methods developed by IES (Illumination Engineering Society). Heat Sink of aluminium housing should be such that LED junction temperature shall not rise above 90 degree C.
2. The OEM of Highmast lighting system shall provide testing certificate for accessories like winch, Motor, ERP Cable , Steel rope etc. to ensure compliance with qualit and safety standards, Minimum overlap distance of different section should be 1.5 times of upper section
3. If the product is not manufactured by OEM in its own factory, the CML no. of associate vendor / manufacturer will be acceptable, provided that there is mutual agreement between both parties, duly intimated to BIS and the site engineer should ensure the same.

## Ch 19 Overhead lines
Chapter E - 19
Over Head Lines
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
19.1 | Supply and erection of P.C.C. pole as per REC manual no 15/1979 (ammended upto date) and as per latest Discom specifications with factor of safety 2.5 including excavation of pit upto pole planting depth 1/6th of pole length. and back filling with stone aggregate/boulders and soil by ramming and watering etc complete as required.
19.1.1 | 8.0 Mtr long of 200 Kg Working Load | Each | 3194 | 278
19.1.2 | 9.0 Mtr long PCC pole of 200 Kg Working Load | Each | 4472 | 389
19.1.3 | 9.0 Mtr long PCC pole of 400 Kg Working Load | Each | 5494 | 478
19.1.4 | 11.0 Mtr long PCC pole of 400 Kg Working Load | Each | 5877 | 511
19.2 | Supply and erection of GI stay set confirming to pattern-1 of BS:16/1974 and as per latest Discom Specifications complete with stay rod with anchor plate fitted with cast iron cross head and steel bow, in cement concrete 1:3:6 including excavation of pit-re-filling etc complete as required.
19.2.1 | Stay set of dia 20mm, 2.4m long stay rod and anchor plate 380 x 380 x 4.0 mm | Each | 1066 | 95
19.2.2 | Stay set of dia 16mm, 1.8m long stay rod and anchor plate 300 x 300 x 4.0 mm | Each | 564 | 50
19.3 | Supply and fixing of following LT Supporting accessories with nut bolt & Clamps made out as per standard Discom's specifications with two coats of Red oxide and two coats of Aluminium paint etc. as required.
19.3.1 | LT cross arm 600 mm long with clamp | Each | 368 | 33
19.3.2 | LT cross arm 1200 mm long with clamp | Each | 586 | 52
19.3.3 | Suspension clamp with eye hook & Pole clamp | Each | 411 | 37
19.3.4 | Dead end clamp with eye hook & Pole clamp | Each | 448 | 39.996
19.3.5 | Type A LT connector for Aerial bunched cable | Each | 61 | 5
19.3.6 | Type B LT connector for Aerial bunched cable | Each | 47 | 4
19.4 | Supply and fixing of LT porcelain pin insulator as per IS 1445-1997 and as per Discom's standard specifications,suitable for working voltage 1100 volts including all accessories like MS Forged GI LT Pin confirming to IS:7935/1975 (latest amended) Nut, Bolt etc. as required.
19.4.1 | 100 mm x 70 mm | Each | 84 | 7
19.5 | Supply and fixing of LT porcelain shackle insulator as per IS:1443 1979 and as per Discom's standard specifications, suitable for working voltage 1100 volts including all accessories like GI Hardware fittings confirming to IS:7935/1975 (latest amended) Nut, Bolt etc. as required.
19.5.1 | 75mm x 90mm | Each | 85 | 8
19.5.2 | 100mm x 110mm | Each | 106 | 9
19.6 | Supplying and drawing Aluminium conductor steel reinforced (ACSR) ISI marked(IS 398 part II-1996) on existing cross arms through insulator with all necessary T&P required including binding and twisting etc. complete in all respect as required.
19.6.1 | 30 Sqmm of (6+1) 2.59mm (Weasel) | Mtr. | 35 | 3
19.6.2 | 50 Sqmm of (6+1) 3.35 mm (Rabbit) | Mtr. | 62 | 6
19.6.3 | 50 Sqmm of (6+1) 3.35 mm (Insulated Rabbit) for LT | Mtr. | 76 | 7
19.6.4 | 80 Sqmm of (6+1) 4.09 mm (Raccon) | Mtr. | 81 | 7
19.6.5 | 100 sqmm of (6/4.72 mm+1/1.57 mm) (Dog) | Mtr. | 112 | 9.999
19.6.6 | ACSR Panther Aluminium 30/3 MM | Mtr. | 212 | 19
19.6.7 | AAA Conductor (Equivelent size Weasel) | Mtr. | 36.1 | 3
19.7 | Supply and fixing of 'V' type cross arms with clamps as per latest Discom specifications made of MS angle (65X65X6)on the existing poles complete including all necessary nut and bolt, clamps with two coats of Red oxide and two coats of Aluminium paint etc. as required. | Each | 1099 | 98
19.8 | Supply and fixing of Galvanised steel 'V' type cross arms with clamps as per latest Discom specifications made of Galvanised steel angle(65x65x6) on the existing poles complete including all necessary nut and bolt, clamps as required. | Each | 1349 | 121
19.9 | Supply and fixing of top hamper on the existing pole as per latest Discom specifications complete including nut bolts with two coats of Red oxide and two coats of Aluminium paint etc as required.
19.9.1 | Vertical type
19.9.1.1 | 11 kV (.7m long) (65 x 65 x6mm angle) | Each | 266 | 24
19.9.1.2 | 11 kV(50 x 6 mm flat) | Each | 161 | 14
19.9.2 | Horizontal type
19.9.2.1 | 11 kV (65 x 65 x6mm angle) | Each | 187 | 17
19.9.2.2 | 11 kV with double top hamper (65 x 65 x 6mm angle) | Each | 236 | 21
19.10. | Supply and fixing of Galvansied top hamper on the existing pole as per latest Discom specifications complete including nut bolts etc as required.
19.10.1 | Vertical type
19.10.1.1 | 11 kV (.7m long) (65 x 65 x6mm Galvanised Steel angle) | Each | 346 | 31
19.10.1.2 | 11 kV(50 x 6 mm Galvanised steel flat) | Each | 147 | 13
19.10.2 | Horizontal type
19.10.2.1 | 11 kV (65 x 65 x6mm Galvanised Steel angle) | Each | 280 | 24.9975
19.10.2.2 | 11 kV with double top hamper (65 x 65 x 6mm Galvanised Steel angle) | Each | 268 | 24
19.11 | Supply and fixing of MS. Channel Bracket 100 mm x 50 mm with clamp as per Discom Specifications including Nut, Bolt with two coats of Red oxide and two coats of Aluminium paint etc. as required.
19.11.1 | 1.8 Mtr. Long | Each | 1548 | 138
19.11.2 | 1.4 Mtr. Long | Each | 1239 | 111
19.12 | Supply and fixing of galvanized steel Channel Bracket 100 mm x 50 mm with clamp as per Discom Specifications including Nut, Bolt with two coats of Red oxide and two coats of Aluminium paint etc. as Required.
19.12.1 | 1.8 Mtr. Long | Each | 2120 | 189
19.12.2 | 1.4 Mtr. Long | Each | 1692 | 151
19.13 | Supply and fixing of 11 kV pin insulator confirming to IS:731:1971 with latest ammendment on existing bracket including all accessories like MS forged hot dipped GI Pin confirming to IS 2486(Part-I)/1993 & IS:2486 (Part-II)/1989 with latest amendment, and as per latest Discom specs. etc. as required. | Each | 166 | 15
19.14 | Supply and fixing of 11kV Disc insulator and Hot dipped galvanized Hardware confirming to IS:731:1971 with latest ammendment and as per latest Discom Specs. on existing bracket including all accessories etc. as required.
19.14.1 | B & S type hardware 45 KN | Each | 622.2 | 55.6
19.14.2 | T & C type hardware 45 KN | Each | 193 | 17.2
19.14.3 | B & S disc insulator 45 KN | Each | 342 | 30.6
19.14.4 | T & C disc insulator 45 KN | Each | 336 | 30
19.15 | Supply and fixing of PG / T clamps on overhead lines/jumpers, made of aluminium alloy 4600 of IS 617-1994 (with latest amendment if any) with steel nut and bolts conforming to IS 1363-1992 & IS 1367/1979-80 (with latest amendments if any) all ferrous metal parts intended for outdoor use except those made of stainless steel shall be protected by hotdip galvanising in accordance with IS 2633-1986 complete in all respect as required.
19.15.1 | PG Clamp for Panther Conductor | Each | 280 | 24.9975
19.15.2 | PG Clamp for Dog Conductor Type - A | Each | 218 | 19
19.15.3 | PG Clamp for Weasel Conductor | Each | 68 | 6
19.15.4 | PG Clamp for Rabbit Conductor | Each | 72 | 6
19.15.5 | T Clamp for Panther Conductor | Each | 324 | 29
19.16 | Supplying and laying of Hot dip galvanized steel stay wire of 550-900 N/mm Quality confirming to IS-2141/2000 in all respect Including chemical composition (Heavily coated Hard quality) of dia 7/3.15 mm(7/10 SWG) and as per latest Discom specs. etc. as required. | Mtr | 93 | 8
19.17 | Supply and fixing of 11 / 33. KV Stay insulator as per IS:5300/1969 and as per Discom's standard specifications etc. as required.
19.17.1 | 110 x 75 x 22mm 11 KV Stay Insulator | Set | 44 | 4
19.17.2 | 140 x 85 x 25mm 33 KV Stay Insulator | Set | 60 | 5
19.18 | Supply and fixing of LT Distribution Kiosk confirming to IS:13947/1993/ IEC 60947 Pt.3 amended up-to-date and as per DISCOM specifications made of 2 mm thick powder coated CRCA sheet of 415 volts 3 phase 4 wire triple pole and neutral type, complete in all respect as required. Including Incoming Switch Disconnector Fuse unit, Aluminium Busbar with copper one piece U contacts base, brass studs and nuts, copper busbar for main and interconnection, MS Channel frame of 75 mm x 40 mm grouted with C.C. of M-10 grade to achieve the height of 1.5 feet above the road level suitable for required no. of outgoing.
19.18.1 | 200 Amp. LT Distribution Kiosk for 63/100 KVA Transformer | Each | 32325 | 2889
19.18.2 | 400 Amp. LT Distribution Kiosk for 250/315 KVA Transformer | Each | 55994 | 5000
19.18.3 | 100 Amp. Distribution Kiosk of Size 500mm x 550 mm x 700 mm suitable for Underground cable | Each | 20905 | 1867
19.19 | Supply and fixing of 11 KV Outdoor 4 way feeder pillar Box confirming to Discom specifications and made of 3.15 mm thick powder coated CRCA sheet enclosure confirming to IS 14772/IEC 60670 (1989) of Size 1000 mm x 1000 mm x 1500 mm, Both front and rear doors should have 3 heavy duty M.S. hinges with Brass pin inserted inside and locking arrangements.The bottom foundation frame stand should be made from 65x65x6mm MS Angle with four legs of 200mm height provided with 150x150x6mm flats grouted with C.C. of M-10 grade to achieve the height of 2.0 feet above the road level suitable for four outgoing. | Each | 51017 | 4555
19.20 | Supply and fixing of 100 Amp, 11kV Horn gap fuse set IS 9385 on existing DP structure with 6 nos 24kV/22kV post insulator (IS:5350 part III), hot dipped hard ware,fuse wire of required size etc. complete in all respect as per Discom specification etc. as required. | Each | 6471 | 578
19.21 | Supply and fixing of 11kV, 400 Amp 3 pole, central pot rotating double break type isolator (IS:9921 part I toV) without earth blade operating mechanism with GI spring loaded reverse loop type fixed contact, solid hard drawn electolytic copper tubular moving contact with silver/ nickel plated at end points, 9 nos post insulator of 12 kV (IS:2554 & IS 5350 part III), hot dipped galvanising hard ware, nut, bolts etc complete in all respect as per Discom specification etc. as required. | Each | 20531 | 1833
19.22 | Supply and fixing of distribution type Lightening arrestor ( Set of 3 Nos.) 9 kV, 10 kA (IS:3070) with mounting breaking to be installed on existing DP structure etc. as required. | Set | 4355 | 389
19.23 | Supply and fixing Substation structure for mounting 11/0.4 Kv Transformer on Double pole as per DISCOM specification complete in all respect as required including nuts and bolts etc (excluding the cost of poles) made of MS channel of 4 nos 100 x 50 x 6mm and 4 nos 75 x 40 x 6mm and MS flat 50 x 6mm etc. as required. | Each | 17669 | 1578
19.24 | Supply and fixing of 1.6 mm thick MS 11 kV Danger plates as per IS :2551-1982 & specification of Discom on the existing poles complete in all respectas as required. | Each | 249 | 22
19.25 | Providing and fixing of single pole mounted substation structure set for isolator / single phase transformer as per DISCOM specification complete in all respect with nuts and bolts as required MS flat 50 x 6mm, MS angle 65 x 65 x6mm, MS channel 100 x 50 x 6mm. ( Excluding cost of pole ). Etc. as required. | Each | 2909 | 260
19.26 | Supply and erection of RS joist of 116 x 100 mm, 11 Meter long with the welded/ bolted top hamper 65 x 65 x 6mm (0.7 Mtr long) making necessary arrangement for fixing 11 kV 'V' cross arm, LT bracket and guard wire bracket, grouted in ground 1/6 th of its length and fixed with cement, coarse and grit in 1:3:6 ratio in 1/5th of its length (40cm dia) from the bottom including two coats of aluminium paint over the complete length of joist etc. as required. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra) | Each | 20531 | 1833
19.27 | Supplying and drawing of XLPE insulated LT Aluminum conductor Aerial bunched cable confirming to IS 14255/1995 and IS 398 (Pt-4)/ 1994 and as per Discom Specs. on existing cross arms through I hook with all necessary T&P required including binding and twisting etc. complete in all respect as required.
19.27.1 | 1 X 25 sq. mm. + 1X25 sq. mm. (Bared) | Mtr | 56 | 5
19.27.2 | 1 X 25 sq. mm. + 1X25 sq. mm. (insulated) | Mtr | 61 | 5
19.27.3 | 3 X 16 sq. mm. + 1X25 sq. mm. (Bared) | Mtr | 68 | 6
19.27.4 | 3 X 16 sq. mm. + 1X25 sq. mm. (insulated) | Mtr | 74 | 7
19.27.5 | 3 X 25 sq. mm. + 1X25 sq. mm. (Bared) | Mtr | 110 | 10
19.27.6 | 3 X 25 sq. mm. + 1X25 sq. mm. (insulated) | Mtr | 117 | 10
19.27.7 | 3 X 50 sq. mm. + 1X35 sq. mm. (Bared) | Mtr | 184 | 16
19.28 | Supply & Erection of M S lattice structure of height 12.8 mtr as per DISCOMs approved design & details in alignment, including painting of tower of approved make two coat of red oxide paint and one coat of aluminium paint before installation and one coat of Aluminium paint after erection work completed as per technical specifications & drawing of DISCOM. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra). | Each | 51110 | 4444
19.29 | Supply & Erection of Galvanised steel lattice structure of height 12.8 mtr as per DISCOMs approved design & details in alignment, including painting of tower of approved make, all completed as per technical specifications & drawing of DISCOM. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra). | Each | 67509 | 5870
19.30. | Supply & Erection of M S lattice structure of height 11.0 mtr as per DISCOMs approved design & details in alignment, including painting of tower of approved make two coat of red oxide paint and one coat of aluminium paint before installation and one coat of Aluminium paint after erection work completed as per technical specifications & drawing of DISCOM. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra) | Each | 42407 | 3688
19.31 | Supply & Erection of Galvanised steel lattice structure of height 11.0 mtr as per DISCOMs approved design & details in alignment, including painting of tower of approved make,all completed as per technical specifications & drawing of DISCOM. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra) | Each | 55904 | 4861
19.32 | Supply of Fabricated 33 KV of 'V' type cross arms made of MS angle(75x75x6 mm) with clamp etc as per Discom specifications on the existing poles complete including all necessary nut and bolt etc with clamps including two coats of Red oxide and two coats of Aluminium paint etc. as required. | Each | 1875 | 88
19.33 | Supply of Fabricated 33 KV of 'V' type cross arms made of Galvanised steel angle (75x75x6 mm) with clamps etc on the existing poles complete including all necessary nut and bolt etc with clamps as required. | Each | 2470 | 115
19.34 | Supply and fixing of top hamper as per Discom specifications on the existing pole complete including nut bolts etc as required. Vertical type 33 kV. 0.75mtr. IS 75x75x6mm as per tech specs. Of DISCOM (Steel weight 6.5Kg. Approx. per top hamper). | Each | 418 | 19
19.35 | Supply and fixing of Galvanised steel top hamper as per Discom specifications on the existing pole complete including nut bolts etc as required. Vertical type 33 kV. 0.75mtr. IS Galvansied angle 65x65x6mm as per tech specs. Of DISCOM (Steel weight 5.8Kg. Approx. per top hamper). | Each | 236 | 15
19.36 | Supply & Erection of special stud structure for 33KV lattice structure as per Discom specifications made of M.S. angle, channer, flats complete in all respects with bracings including painting of tower of approved make two coat of red oxide paint and one coat of aluminium paint before installation and one coat of Aluminium paint after erection work completed as per technical specifications & drawing of DISCOM. (Excavation of pit PCC and CC foundation as per Discom specs. to be Paid Extra). | Each | 21720 | 1889
19.37 | Supply and fixing of 33 kV pin insulator confirming to IS:731:1971 with latest ammendment on existing bracket including all accessories like MS forged hot dipped GI Pin confirming to IS 2486(Part-I)/1993 & IS:2486 (Part-II)/1989 with latest amendment, and as per latest Discom specs. etc. as required. | Each | 485 | 23
19.38 | Supply and fixing of 33kV Disc insulator and Hot dipped galvanized Hardware confirming to IS:731:1971 with latest ammendment and as per latest Discom Specs. on existing bracket including all accessories etc. as required.
19.38.1 | B & S type hardware 120KN | Each | 951 | 44
19.38.2 | B & S disc insulator 120KN | Each | 808 | 38
19.39 | Supply and fixing of guard bracket 2.2 mtr. long made from (75x40) ISMC 7.14Kg. Per Mtr. M.S. channel including necessary clamp and botls etc. as per technical specification & drawing of DISCOM. | Each | 1271 | 113
19.40. | Supply and fixing M.S. channel (cut point) 100x50mm ISMC (9.5Kg. Per Mtr.) 2x1.8mtr. long with pilot patti 50x6mm thick necessary nuts and bolts etc. as per technical specification & drawing of DISCOM. | Each | 3127 | 279
19.41 | Supply and installation of spike of M.S. rod 20mm dia 3.0mtr. long for earthing of (tower/pole) drive into earth by mechanical means sturcture connection the spike with cross arm top hamper PCC pole, lattics tower to earth etc. complete as per technical specification of DISCOM. | Each | 1618 | 144
19.42 | Labour charges for Dismantling the structure with pole mounted transformer of different capacity along with distribution boards and re- erecting the transformer on newly erected structure along with distribution boards and including testing and commissioning (as well as cabling connection complete as required) | Job |  | 2866
19.43 | Labour charges for dismantling of existing PCC/MS electrical Pole including MS channel, V cross arm, 11KV insulator, LT insulator, guard wires, stay wires, one span of ACSR conductors and other electric items, coming along and in the alignment of the road, then removal and re-rolling of the PCC /MS Pole as well as other materials and handing over the same to DISCOM store including transportation from site to store and stacking of dismantling material in store and as per the direction of Engineer Incharge, clean the site good as per the requirement and dismantle material receipt duly signed by DISCOM Engineer submit the receipt to EIC as required. | Per pole |  | 1172
19.44 | Labour charges for dismantling of existing Lattice tower including MS channel, V cross arm, 11KV/33 KV insulator, guard wires, stud/stay wire, one span of ACSR conductor and other electric items coming along and in the alignment of the road, then removal and re-rolling of Lattice tower as well as other materials and handing over the same to DISCOM store including transportation from site to store and stacking of dismantling material in store and as per the direction of Engineer Incharge and clean the site good as per the requirement and submit the receipt from DISCOM/ concering authority complete as required. | Per lattice tower |  | 1555.4
19.45 | Labour charges for dismantling of existing street light electrical pole with street light fixture, underground cable, MS box and other electric items of the pole coming along and in the alignment of the road, then removal and re- rolling of MS/PCC pole of different sizes as well as other materials and handing over the same to DISCOM/UIT/MC store and as per the direction of Engineer Incharge and clean the site good as per the requirement and submit the receipt from concering authority complete as required. | per pole |  | 655
19.46 | Labour charges for dismantling of service line connection (weather proof cable/armoured cable) for single phase /three phase supply of industrial/domestic connections from existing PCC/MS pole and handing over the same to DISCOM store including transportation from site to store and stacking of dismantling material in store and provide temporary supply to domestic/industrial connections to the consumer where supply is disconnected and clean the site good as per the requirement and direction of Engineer Incharge complete as required. | Job |  | 167
19.47 | Labour charges for Trimming of tree branches/plants and prepairing route approaches for electric proposed line complete with prior permission of local authority in writing , taking proper shutdown from discom office and inform to DISCOM after complete the work. | Job |  | 49.995

## Ch 20 ELV Works
Chapter E - 20
ELV Works
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
Local Area Networking
20.1 | Supply, Drawing and Testing of 4 pair, 23 AWG Solid Bare Copper wire insulated with PVC, U/UTP (Unscreened/Unshielded Twisted Pair), Category 6, Class E, 100 Ohm Impedance, Indoor Cable as per latest ammendments of ANSI/TIA/EIA-568 , The copper conductors should be balanced twisted in pairs, seperated by a cross-member fluted pair divider & protected by LSZH Jacket. Certified performance in a 4-connector configuration upto 100 Mtrs channel requirements & transmission frequencies ranging from 250 to 500 Mhz. in existing MS/PVC Conduits/casing capping including making connections to Information outlets and Patch Panels with jack & ferruling at both ends for identification with necessary tools for punching, stripping, crimping and testing etc as required complete in all respect. | Mtr. | 44 | 6
20.2 | Supply, Drawing and Testing of 4 pair, 23 AWG Solid Bare Copper wire insulated with HDPE, U/UTP (Unscreened/Unshielded Twisted Pair), Category 6, Class E, 100 Ohm Impedance, Outdoor ECCS armoured Cable as per latest ammendments of ANSI/TIA/EIA-568 C.2 & ISO/IEC 11801 2nd Ed, The copper conductors should be balanced twisted in pairs, seperated by a cross divider & protected by PVC outer jacket of UV resistant. Certified performance in a 4-connector configuration upto 100 Mtrs channel requirements & transmission frequencies ranging from 250 Mhz to 500 Mhz. Should meet IEEE 802.3af & IEEE 802.3at for POE applications. Cable Should support Ethernet 10GBASE-T according to the standards. in existing MS/PVC Conduits/casing capping including making connections to Information outlets and Patch Panels with jack & ferruling at both ends for identification with necessary tools for punching, stripping, crimping and testing etc as required. | Mtr. | 82 | 10
20.3 | Supply, Drawing and Testing of 4 pair, 23 AWG Solid Bare Copper wire insulated with HDPE, Category 6A/Class Ea, U/FTP (Unshielded/Foiled Twisted Pair), 100 Ohm Impedance, Indoor Cable as per latest ammendments of ANSI/TIA/EIA-568 C.2 & ISO/IEC 11801 2nd Ed, The copper conductors should be balanced twisted in pairs, Shielded and Aluminum Foil Sheilding of Individual pairs protected by PVC Jacket. Certified performance in a 4-connector configuration upto 100 Mtrs channel requirements & transmission frequencies 500 Mhz. Should meet IEEE 802.3af & IEEE 802.3at for POE applications. Cable Should support Ethernet 10GBASE-T according to the standards. in existing MS/PVC Conduits/casing capping including making connections to Information outlets and Patch Panels with jack & ferruling at both ends for identification with necessary tools for punching, stripping, crimping and testing etc as required. | Mtr. | 86 | 11
20.4 | Supply and Installation of unshielded/360 degree shielded PCB based Information outlets made of high impact plastic body with ABS, Flammability rating UL 94 V-0 with provision for protection against dust in jack or Faceplate, suitable for Cat 6/6A application complying to latest amendments, According. to Cat. 6/6A channel, It should support channel as well as components requirements of Cat 6/6A standards at frequencies 250/ 500 MHz. Cat 6/6A unshielded/shielded Jack should be suitable to terminate 4 pair, 23/24 AWG solid/stranded wire diameters, using 100 Ohm unshielded/shielded balance twisted pair cable, the jack should have toolless/impact termination on reliable copper tin plated Insulation displacement contact, with easy lock mechanism, It supports IEC 60603-7-4 and complied with ANSI/TIA 568 C.2 & ISO/IEC 11801 or latest standard. jack should be RJ11,RJ12 & RJ45 compatible. Should support Ethernet 1.2 Gb/s ATM,Digital video and broadband/baseband analog video, Voice over internet protocol (VOIP) Specifications in existing modular/MS Boxes along with necessary connections as required. All as per pre approved by Engineer in charge.
20.4.1 | Cat 6, Un-sheilded Information Outlet | Each | 287 | 84
20.4.2 | Cat 6A, Sheilded Information Outlet | Each | 520 | 84
20.5 | Supply & fixing of square Faceplate for Flush / Surface Mount Information Outlets Single/Dual or Quad Aperture with dust cover, material should be High-impact, flame retardant, thermoplastic, UL listed material, Suitable for RJ45 unshielded/shielded connection modules. Should match with I. O. OEM. Dimensions should be 86mm X 86mm as required complete in all respect. All as per pre approved by Engineer in charge.
20.5.1 | Single Aperture | Each | 88 | 11
20.5.2 | Dual Aperture | Each | 97 | 11
20.5.3 | Quad Aperture | Each | 107 | 11
20.6 | Supply, Installation, Testing and Commissioning of Rack mounted 19" 1U, 24 Port loaded, CRS chasis, powder coated, sheet steel, High-impact, flame retardant, thermoplastic, UL Listed, Modular Patch Panels with Rear Cable management system and mounting hardware to mount the patch panel. Should have port identification numbers printed/engraved on front of the panel. Etc. as required. All as per pre approved by Engineer in charge.
20.6.1 | Modular Patch Panel Loaded with Cat -6 I/O | Each | 7128 | 556
20.6.2 | Modular Patch Panel Loaded with Cat -6A I/O | Each | 11888 | 556
20.7 | Supply , Installation and Testing of 4 pair, 100 Ohm impedance, Cat 6/6A /Class E/Ea patch cords should be constructed of minimum 23/24 AWG, stranded bare Copper cable with LSZH Jacket, with an enhanced performance by factory moulded RJ45 connectors with strain relief boots as per ANSI/TIA/EIA 568-C.2 suitable for Cat 6/6A application complying to latest ammendments Category 6/6A Standards, According. to TIA568C.2, ISO/IEC 11801, EN 50173, IEC 60603-7-51, EN 60603-7, IEEE 802.3an minimum requirement for 1G BASE-T to 10G BASE-T performance. Patch cords shall be straight thru cable compatible with both T568-A and T568-B wiring schemes, should support IEEE 802.3af / IEEE 802.3at for POE applications, Minimum 750 to 1000 mating cycles in plug contacts for long durability, Should support Ethernet 10GBASE-T, 1.2 Gb/s ATM, Token ring 4/16, Digital video and broadband/baseband analog video, Voice over internet protocal (VOIP).
20.7.1 | Cat 6, U/UTP (Unscreened/Un-sheilded Twisted Pair) Patch Cord
20.7.1.1 | 0.50 Mtr | Each | 158 | 11
20.7.1.2 | 1 Mtr | Each | 204 | 11
20.7.1.3 | 2 Mtr | Each | 243 | 11
20.7.1.4 | 3 Mtr | Each | 323 | 11
20.7.2 | Cat 6A, U/FTP (Unscreened/Foiled Twisted Pair) Patch Cord
20.7.2.1 | 0.50 Mtr | Each | 272 | 11
20.7.2.2 | 1 Mtr | Each | 379 | 11
20.7.2.3 | 2 Mtr | Each | 476 | 11
20.7.2.4 | 3 Mtr | Each | 589 | 11
20.8 | Supply, Drawing and OLTS Testing, of OM2 Multi mode (50/125 µm) glass optic fiber cable, as per latest ammendments of TIA/EIA 568/ISO/IEC 11801:2011/ IEC 60794-1-2 E1, E3,E11, F1/ EN 50173-1/ EN 187 000/ IEC 60974-2, 2-20, 2-21/ ITU G.651 with outer sheath, cable should be used for LAN and WAN back bones, for indoor/outdoor installations these sheathed cable be placed in existing MS/PVC /HDPE Conduits/ slotted channels with ferruling at both ends for identification complete in all respect.
20.8.1 | 6 fiber | Mtr. | 107 | 22
20.8.2 | 12 Fiber | Mtr. | 147 | 22
20.8.3 | 24 Fiber | Mtr. | 209 | 22
20.9 | Supply, Installation, OTDR/OLTS Testing & Fusion Splicing of Fiber OM2 Multimode Pigtail (50/125 µm) made of glass fiber optic, should be fitted at one end with any one type of single SC/LC/SN/CS type connector in acc., as per latest ammendments of TIA/EIA 569 Standard Specification as per requirments complete in all respect. | Each | 1099 | 306
20.10 | Supply, Installation, & Testing of Indoor duplex OM2 Multimode patch cord (50/125 µm made of glass fiber optic with LSZH jacket, 2.0x4.1 mm, Multimode ITU G 651 Mounted on both sides with SC/LC/SN/CS type Duplex connectors in acc. with IEC 61754-20. Zirconia (ceramic) ferrule with a PC polished endface geometry, connectors should be tuned in accordance with IEC 61755-3-1 and qualified in acc. with IEC 61753-1 for category U (uncontrolled environment, duplex clip and white plastic dust cover, should comply to delta IL < 0.2 dB after 500 mating cycles, there should be an optional Visual coding, mechanical coding and lock protection on the patch cords which can be added on later stage. patch cords's performance should be acc. to IEC 61753-1 (Table A.12) as per latest ammendments of TIA/EIA 569B.3, as per requirements.
20.10.1 | 1 Mtr | Each | 1415 | 56
20.10.2 | 2 Mtr | Each | 1585 | 56
20.10.3 | 3 Mtr | Each | 1812 | 56
20.10.4 | 5 Mtr | Each | 2175 | 56
20.11 | Supply, Installation, & Testing of 19" 1U Rack Mounted/ surface mounted aluminum/ CRCA powder coated, OM2 multimode glass Fiber Optic Cable Patch panel/LIU loaded with flangeless/screwable adapters for SC/LC/SN/CS type, It should have easy removable Top plate with push buttons, there should be a splice tray installed in the Patch panel/LIU which can handle the fiber cores, splice tray should be PC+ABS material, it should include accessories like mounting hardware, gormetts, heat shrink tubes/sleeves, screws, nuts to install the panel for rackmount applications as per requirement. All as per pre approved by Engineer in charge.
20.11.1 | Multi Mode LIU 6 Ports | Each | 6282 | 389
20.11.2 | Multi Mode LIU 12 Ports | Each | 9055 | 556
20.11.3 | Multi Mode LIU 24 Ports | Each | 12621 | 722
20.12 | Supply, Drawing and OLTS Testing, of stranded OS2 Single mode (9/125 µm) glass optic fiber cable G652D as per latest ammendments of TIA/EIA 568/ISO/IEC with outer sheath, cable should be used for LAN and WAN back bones, for indoor/outdoor installations these sheathed cable be placed in existing MS/PVC /HDPE Conduits/ slotted channels with ferruling at both ends for identification complete in all respect.
20.12.1 | 6 fiber | Mtr | 70 | 22
20.12.2 | 12 Fiber | Mtr | 99 | 22
20.12.3 | 24 Fiber | Mtr | 164 | 22
20.13 | Supply, Installation, OTDR / OLTS Testing & Fusion Splicing of Fiber Singlemode Pigtail (9/125 µm (OS2) made of glass fiber optic, with semi-tight buffer PA/PBT, Ø 0.9 mm, yellow, singlemode G652.D (9/125 µm (OS2), should have length of min 1.5m, should be fitted at one end with any one type of single SC/LC/SN/CS type connector in acc. with IEC 61754-20, Should be delta IL < 0.2 dB after 500 mating cycles, It should be Zirconia (ceramic) ferrule with a PC polished endface geometry connector qualified in acc. with IEC 61753-1 for category U (uncontrolled environment). and qualified in acc. with IEC 61753-1, Performance acc. to IEC 61753-1 (Table A.12) as per latest ammendments of TIA/EIA 569B.3, Standard Specification as per requirements. | Each | 731 | 306
20.14 | Supply, Installation, & Testing of Indoor duplex Singlemode patch cord (9/125 µm (OS2) made of glass fiber optic with LSZH jacket, F8 2.0x4.1 mm, yellow, singlemode G652.D (9/125 µm (OS2) Mounted on both sides with SC/LC/SN/CS type Duplex connectors in acc. with IEC 61754-20. Zirconia (ceramic) ferrule with a PC polished endface geometry, connectors should be tuned in accordance with IEC 61755-3-1 and qualified in acc. with IEC 61753-1 for category U (uncontrolled environment, duplex clip and white plastic dust cover, should comply to delta IL < 0.2 dB after 500 mating cycles, there should be an optional Visual coding, mechanical coding and lock protection on the patch cords which can be added on later stage. patch cords's performance should be acc. to IEC 61753-1 (Table A.12) as per latest ammendments of TIA/EIA 569B.3, as per requirements.
20.14.1 | Single Mode Patch Cord 1 Mtr. | Each | 1245 | 56
20.14.2 | Single Mode Patch Cord 2 Mtr. | Each | 1415 | 56
20.14.3 | Single Mode Patch Cord 3 Mtr. | Each | 1540 | 56
20.14.4 | Single Mode Patch Cord 5 Mtr. | Each | 1869 | 56
20.15 | Supply, Installation, & Testing of 19" 1U Rack Mounted/ surface mounted aluminum/ CRCA powder coated, OS2 Single mode glass Fiber Optic Cable Patch panel/LIU loaded with flangeless/screwable duplex adapters for SC/LC/SN/CS type, It should have easy removable Top plate with push buttons, there should be a splice tray installed in the Patch panel/LIU which can handle the fiber cores, splice tray should be PC+ABS material, it should include accessories like mounting hardware, gormetts, heat shrink tubes/sleeves, screws, nuts to install the panel for rackmount applications as per requirement complete in all respect. All as per pre approved by Engineer in charge.
20.15.1 | 6 Ports | Each | 5828 | 389
20.15.2 | 12 Ports | Each | 8488 | 556
20.15.3 | 24 Ports | Each | 10921 | 722
20.16 | Supply & Installation of IP-20 & IK-08 , Wall mounted Double Section Communication enclosure (Rack) made from powder coated (60 to 80 Micron) CRCA sheet, front sturdy sheet steel frame folded from one piece and welded with minimum 5mm toughened glass door,Vertical Mounting Rail 1.6 MM with 'U'Marking , with All round protective channel on the door aperture, lock integrated on front door, top and bottom cover with cable entry provision with gland plates, integrated side walls, 2 pair of 19" angles with wall mounting provision on wall. Accessories like: 1 No of 19" 1U Horizontal Cable manager, 1 No of 90 cfm 230V AC Fan with 1 mts long cable, mounting hardware , 1 No of 19" 1U, mountable socket strips with 5 nos of 5A universal sockets with 2 mts long power chord for supplying power to switches, fans etc along with earth continuity kit, indicator, moulded power supply cable. fixing on wall with Suitable Anchor fastner etc as required.
20.16.1 | 6 U Rack with Width 600 mm & Depth 400 mm + 100 mm | Each | 9055 | 556
20.16.2 | 9 U Rack with Width 600 mm & Depth 400 mm + 100 mm | Each | 11389 | 556
20.16.3 | 12 U Rack with Width 600 mm & Depth 400 mm + 100 mm | Each | 14263 | 778
20.16.4 | 15 U Rack with Width 600 mm & Depth 400 mm + 100 mm | Each | 16749 | 1111
20.17 | Supply & Installation of IP-20 & IK-08 , Communication enclosure (Rack) made from powder coated (60 to 80 Micron) CRCA sheet,Vertical Mounting Rail 1.6 MM with 'U'Marking, front sturdy sheet steel frame folded from one piece and welded with 5mm toughened glass door, with All round protective channel on the door aperture, lock integrated on front door, top and bottom cover with cable entry provision with gland plates, integrated side walls, Set of 75 mm height 4 castors, 2 of which have brakes, Accessories like: 5 Nos of 19" 1U Horizontal Cable manager, 2 Nos of vertical cable managers, 1 no. Keyboard Tray, 4 Nos of 90 cfm 230V AC Fan with 1 mts long cable, mounting hardware , 2 No of 19" 1U, mountable socket strips with 6 nos of 5A universal sockets with 2 mts long power chord for supplying power to switches, fans etc along with earth continuity kit, indicator, moulded power supply cable complete in all respect.
20.17.1 | 17 U Rack with Width 600 mm & Depth 800 mm | Each | 26212 | 1111
20.17.2 | 22 U Rack with Width 600 mm & Depth 800 mm | Each | 31141 | 1111
20.17.3 | 27 U Rack with Width 600 mm & Depth 800 mm | Each | 35216 | 1333
20.17.4 | 36 U Rack with Width 600 mm & Depth 800 mm | Each | 42242 | 1333
20.17.5 | 42 U Rack with Width 600 mm & Depth 800 mm | Each | 509662 | 1666
20.17.6 | 42 U Rack with Width 800 mm & Depth 1000 mm with 3 no. Heavy Duty Sliduing Drawer | Each | 75315 | 2222
20.18 | Supply , Installation, Testing and Comissioning of Unmanaged Switch Plug-and-play - easy setup with no configuration or no software needed, following Port fast ethernet - 8 port 10/100/1000 MBPS auto-negotiation RJ45 ports, IEEE 802.3x flow control ,supports auto-MDI/MDIX, eliminating the need for crossover cables including making connection etc as required complete in all respect.
20.18.1 | 8 Port | Each | 4188 | 222
20.18.2 | 16 Port | Each | 7135 | 222
20.18.3 | 24 Port | Each | 10194 | 222
20.19 | Supplying, installation, Testing and commissioning of following capacity 8 port Non POE Layer 2 indoor Network Switch having features and specifications etc. as mentioned here under: Minimum 8 X RJ-45 Gigabit Ethernet Ports and additional 2 X 1G SFP Ports with non-blocking architecture by having Switching capacity of minimum 20Gbps and packet forwarding rate of 14Mpps or higher, 8K MAC table. Internal dual AC Power supply with operating temperature of -5 0C to +50 0C. Jumbo frame: 10KB or higher, IGMP Snooping, IGMP snooping querier and support for IGMP Snooping Fast Leave, Should create 250 or more MLD groups, MLD Snooping, Per VLAN MLD Snooping C MLD Snooping Fast Leave, STP, RSTP, MSTP, Loopback detection, Multicast filtering, VLAN Tagging, ǪOS: 8 Ǫue per port, WRR, IPv4/IPv6 Interface : minimum 100 IPv4 static route entries and minimum 50 IPv6 static route entries, 700 Acess Control entries, SSH CSSL for IPv4 and IPv6, 802.1x, ARP Spoofing, DHCP Snooping and server screening, IP+MAC+Port Binding, Per Port Bandwidth Control, 802.1X Authentication (Supports local/RADIUS database, Port-based Access Control and EAP, OTP, TLS, TTLS, PEAP Support) Cable Diagnostic feature, LLDP, LLDP-MED, SNTP/NTP, RMON, SNMP v1,v2c, v3 and SNMP Traps. Certifications: UL, CE, FCC, RoHS, MTCTE, OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 29703 | 2222
20.20. | Supplying, installation, Testing and commissioning of following capacity 8 port PoE Layer 2 Indoor Network Switch having features and specifications etc. as mentioned here under: At least 8 X RJ-45 PoE/PoE+ Gigabit Ethernet Ports and additional 4 X 1G SFP Ports with non-blocking architecture by having Switching capacity of min. 24Gbps and packet forwarding rate of 17Mpps or higher, console port, 16K MAC table, IPv4 and IPv6 ready, IGMP snooping v1, v2, v3, DHCP,DHCP Relay, NTP/SNTP, SNMPv1, v2 C v3, TELNET/ SSH, LACP, STP, RSTP, MSTP, ERPS. VLAN: Port based, Mac based, IP subnet based, tag based, protocol based. Ǫ- in Ǫ, L2/L3 ACL, 1588v2 Precision Time Protocol HW- Based E2E Transparent clock, SNTP, TFTP, SNMP, Radius, Syslog. Dual DC Power input, IP30 rated, DIN Rail, -5° to 70° C operating temperature. Certificate: UL, CE, FCC, NEMA-TS2, IEC/MIL-STD for Shock , Vibration & Drop Certificate. OEM Should have Certificate for Industrial Cyber Security Capability IEC- 62443-4-1:2018, ISO 45001, ISO 27001 and ISO 14001 Certified or Equivalent Indian Certificate. OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 39780 | 2222
20.21 | Supplying, installation, Testing and commissioning of following capacity 24 port Non POE Layer 2 indoor Network Switch having features and specifications etc. as mentioned here under: At least 24 X RJ-45 Gigabit Ethernet Ports and additional 2 X 10G Base -T with 4 X SFP Ports with non-blocking architecture by having Switching capacity of min. 168Gbps and packet forwarding rate of 125Mpps or higher, 16K MAC table. Console Port, USB port, Stacking support of min. 8 units per stack. Internal dual AC Power supply, STP, RSTP, MSTP, BPDU Filter, BPDU Restriction, Min. 9K Jumbo Frame, LBD, IGMP Snooping V1/V2/V3, MLD Snooping V1/V2. IGMP /MLD Groups 1K or more, IPv4/IPv6 Loopback Interface, 16 L3 IP Interface, Ipv6 ND, VRRPv3, UDP Helper, ECMP. VLAN: 802.0Ǫ, Port based, Ǫ-in-Ǫ, Multicast VLAN, Protocol VLAN, VLAN Trunking, DHCP Snooping, Server, server Screening. RADIUS , TACACS+ Authentication, ǪoS: 802.0P, 8 queues per port, ǪoS : WRR, Strict+WRR, WRED, 802.0p. ACL: MAC based, IPv4C IPv6, TCP/UDP Port number, time based ACL, TFTP Client, SNMP V1, v2c, v3, SNMP traps, RMON, DHCP server, relay, client, LLDP, LLDP-MED, OAM, Dying Gasp, 802.0ah, sflow, RIP, OSPF v2/v3, policy based route, SSL, SSH. 6 kV surge protection on all Gigabit Ethernet ports and on all GE RJ-45 access ports. Certifications: UL, CE, FCC, RoHS, MTCTE, OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 90151 | 3333
20.22 | Supplying, installation, Testing and commissioning of following capacity 24 port POE Layer 2 indoor Network Switch having features and specifications etc. as mentioned here under: At least 24 X RJ-45 Gigabit Ethernet Ports and additional 2 X 10G Base -T with 4 X SFP Ports with non-blocking architecture by having Switching capacity of min. 168Gbps and packet forwarding rate of 125Mpps or higher, 16K MAC table. Console Port, USB port, Stacking support of min. 8 units per stack. Internal dual AC Power supply, STP, RSTP, MSTP, BPDU Filter, BPDU Restriction, Min. 9K Jumbo Frame, LBD, IGMP Snooping V1/V2/V3, MLD Snooping V1/V2. IGMP /MLD Groups 1K or more, IPv4/IPv6 Loopback Interface, 16 L3 IP Interface, Ipv6 ND, VRRPv3, UDP Helper, ECMP. VLAN: 802.0Ǫ, Port based, Ǫ-in-Ǫ, Multicast VLAN, Protocol VLAN, VLAN Trunking, DHCP Snooping, Server, server Screening. RADIUS , TACACS+ Authentication, ǪoS: 802.0P, 8 queues per port, ǪoS : WRR, Strict+WRR, WRED, 802.0p. ACL: MAC based, IPv4C IPv6, TCP/UDP Port number, time based ACL, TFTP Client, SNMP V1, v2c, v3, SNMP traps, RMON, DHCP server, relay, client, LLDP, LLDP-MED, OAM, Dying Gasp, 802.0ah, sflow, RIP, OSPF v2/v3, policy based route, SSL, SSH. 6 kV surge protection on all Gigabit Ethernet ports and on all GE RJ-45 access ports. Certifications: UL, CE, FCC, RoHS, MTCTE, OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 117823 | 3333
20.23 | Supplying, Installation, Testing and commissioning of small form-Pluggable (SFP) for Network Switches. Must be hot Pluggable, RoHS Complaint, etc. complete as required.(For Each SM Fiber) all switches & related Fiber modules should be of same make & category for seamless integration with each other of Enterprise class.
20.23.1 | 1G SFP Single Mode/Multi Mode | Each | 3562 | 111
20.23.2 | 1G Copper SFP | Each | 5936 | 111
20.23.3 | 10 G SFP + Single Mode/Multi Mode | Each | 10783 | 278
20.24 | Supply, installation, Testing and Commissioning of 1000 base-LX/LH single mode/Multi mode fibre to 1000 base-T copper giga bit , Media Convertor complete as required complete in all respect. | Each | 3389 | 556
20.25 | Fiber Fusion Splicing with OTDR/OLTS Testing of Fiber Single/ Multi mode (per splice) of glass Fiber Optic Cable including jointer box and cleaning the cable and making splice as per standard practice complete in all respect. | Each | 696 | 333
20.26 | Supplying, Installation, Testing and commissioning of indoor Wireless Access Point for Low Density use having features and specifications etc. as mentioned here under - Dual-band Wi-Fi6 (802.11ax) 574Mbps (2.4GHz) + 1200Mbps (5GHz), WI-FI 6 Certified, 1 x RJ45 console port, 1G LAN POE Port, factory reset, WPA/WPA2/WPA3TM Personal/Enterprise, WEP 64/128-bit, SSID broadcast disable, MAC address access control, Internal RADIUS server, SNMP, Customizable Captive Portal, Auto Channel, Works as Access Point, WDS, WDS with AP, Wireless Client, Web (HTTP), Secure Socket Layer (SSL), Traffic control, Support ATF/Fast Roaming/Band Steering, Supports enhanced security – WPA-PSK/WPA2- PSK/WPA3-PSK and RADIUS client, and Cipher negotiation, and MAC/ IP ACL for networks, Certifications: MTCTE, CE, FCC. Should also work as Standalone and must be Compatible with S/W & H/W Controller with addtional features like - Real-Time Monitoring and Alerts, Rich Advanced Features, Centralized Device Management, Role-Based Administration, Real-Time Monitoring, VLAN and Access Control, Auto RF Management and Bandwidth Optimization, Multi-SSID and Captive Portal Authentication.OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 19254 | 556
20.27 | Supplying, Installation, Testing and commissioning of indoor Wireless Access Point for High density use having features and specifications etc. as mentioned here under- WiFi6 802.11ax 574Mbps (2.4GHz) + 2402Mbps (5GHz), WIFI 6 Certified, 1 x RJ45 console port, MG 2.5G LAN POE Port, factory reset, WPA/WPA2/WPA3TM Personal/Enterprise, WEP 64/128-bit, SSID broadcast disable, MAC address access control, Internal RADIUS server, SNMP, Customizable Captive Portal, Auto Channel, Works as Access Point, WDS, WDS with AP, Wireless Client ., Web (HTTP), Secure Socket Layer (SSL), Traffic control, Support ATF/Fast Roaming/Band Steering, Supports enhanced security – WPA-PSK/WPA2- PSK/WPA3-PSK and RADIUS client, and Cipher negotiation, and MAC/ IP ACL for networks, Certifications: MTCTE, CE, FCC. Works as Standalone, Compatible with S/W & H/W Controller with addtional features like - Real-Time Monitoring and Alerts, Rich Advanced Features, Centralized Device Management, Role-Based Administration, Real-Time Monitoring, VLAN and Access Control, Auto RF Management and Bandwidth Optimization, Multi-SSID and Captive Portal Authentication.OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 29453 | 556
20.28 | Supplying, Installation, Testing and commissioning of Outdoor Wireless Access Point having features and specifications etc. as mentioned here under - WIFI 6 Certified, 1 x RJ45 console port, MG 2.5G LAN POE Port, factory reset, 4 x internal antennas, the transmission coverage of shall be minimum 80 meters in radius, AP should have transmission power minimum of 22 dBm, The AP shall provide a minimum of 29 dBm EIRP for both 2.4 GHz and 5 GHz frequencies. Field deployment shall be with EIRP as per regulatory guidelines, AP shall have dual-band Omni-directional Antenna, either internal or external. Field deployment shall be with EIRP as per the WPC guideline, WPA/WPA2/WPA3TM Personal/ Enterprise, WEP 64/128-bit, SSID broadcast disable, MAC address access control, Internal RADIUS server, SNMP, Customizable Captive Portal, Auto Channel, Works as Access Point, WDS, WDS with AP, Wireless Client, Web (HTTP), Secure Socket Layer (SSL), Traffic control, Support ATF/Fast Roaming/Band Steering, Supports enhanced security – WPA- PSK/WPA2-PSK/WPA3-PSK and RADIUS client, and Cipher negotiation, and MAC/ IP ACL for networks, IP68 water/dustproof standard, 6KV Surge Protection; 4KV ESD Protection (contact), 6KV (air), Operating ambient temperature (-5~50 °C), Grounding point support, IEC 60601-1-2 EMC Medical Electrical Equipment Testing and Certification, EN50121-1 & EN50121-4 for Wireless Application. Certifications: MTCTE, CE, FCC. Works as Standalone, Compatible with S/W & H/W Controller with additional features like - Real-Time Monitoring and Alerts, Rich Advanced Features, Centralized Device Management, Role- Based Administration, Real-Time Monitoring, VLAN and Access Control, Auto RF Management and Bandwidth Optimization, Multi-SSID and Captive Portal Authentication. OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. as required. | Each | 39028 | 556
20.29 | Supplying, Installation, Testing and commissioning of indoor Wireless Controller having features and specifications etc. as mentioned here under- The network controller shall be a dedicated hardware appliance designed for centralized management of wireless access points, It must support the management of up to 500 networking devices, The system should be on-premise, ensuring data privacy and complete control over network configurations. It must include an intuitive user interface for real-time monitoring, device discovery, firmware upgrades, scheduling, and mass configuration deployment. Features such as role-based administration, multi-site management. AP to controller communication shall be use of industry standards-based (IEEE or IETF) CAPWAP or any tunneling protocols as per guidelines of DoT.The controller should support Layer 2 and Layer 3 device discovery, VLAN configuration, MAC ACL groups, IGMP snooping, and bandwidth optimization. Automatic radio frequency (RF) management and access policy enforcement are required for reliable wireless performance. The solution must offer a comprehensive dashboard with network topology, floor plan views, client and device lists, and alert notifications. For authentication, it should support a range of methods including local database, external RADIUS, LDAP, and passcode or MAC-based access. It should provide detailed traffic analytics, logs, and customizable reporting for network visibility and planning. Firmware and configuration backup and restoration functions must be available, with USB- based log storage supported. Physical specifications should include a compact form factor with a minimum of one 2.5G Ethernet port and USB 3.0 port, and it must be MTCTE,CE, FCC, and RoHS certified. The controller should operate reliably within a 0°C to 40°C temperature range and 10–90% non-condensing humidity. /Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required. | Each | 90728 | 2222
0 | 0 | per Node |  | 111
CCTV Survelience system
20.31 | SITC of IP Based 2MP Dome camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution: (1920 x 1080) @30 fps of following lens size and IR Range. The camera should support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps,120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), onboard storage upto 512 GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM . Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered, Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.31.1 | 2.8/3.6/4 mm lens with 30 meter IR range | Each | 6624 | 556
20.31.2 | 6/8 mm Lens morethan 30 to 50 meter or above IR range | Each | 8150 | 556
20.32 | SITC of IP Based 2MP Bullet camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution: (1920 x 1080) @30 fps, (As per site requirement). Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.32.1 | 2.8/3.6/6/8 mm lens with 50 Meter IR OR Higher | Each | 8959 | 56
20.33 | SITC of IP Based 2MP Dome camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution: (1920 x 1080) @30 fps with a varifocal 2.8mm to 12mm lens or better. Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, IR Range - 40mtr or higher, 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 15050 | 556
20.34 | SITC of IP Based 2MP Bullet camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution: (1920 x 1080) @30 fps with a varifocal 2.8mm to 12mm lens or better. Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, IR Range - 50mtr or higher, 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have service/ support center in Rajasthan. | Each | 16484 | 556
20.35 | SITC of IP Based 5MP Dome camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution:(2560 x 1920) @30 fps. Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection, and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.35.1 | 2.8/3.6/4 mm lens with 30 meter IR range | Each | 11958 | 556
20.35.2 | 6/8 mm Lens more than 30 to 50 meter or above IR range | Each | 13935 | 556
20.35.3 | Varifocal 2.8mm to 12mm lens or better with 40 Meter IR Range or higher | Each | 22170 | 556
20.36 | SITC of IP Based 5MP Bullet camera: 1/2.8" or larger Progressive Scan CMOS Sensor with resolution:(2560 x 1920) @30 fps Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.36.1 | 2.8/3.6/4/6/8 mm lens IR Range - 50mtr or higher, | Each | 14975 | 556
20.36.2 | Varifocal 2.8mm to 12mm lens or better with 50 Meter IR Range or higher | Each | 24453 | 556
20.37 | SITC of IP based 8MP 4K Ultra HD Dome camera with 1/2.8" or larger Progressive Scan CMOS Sensor with resolutions up to 3840 × 2160 (4K) @30 fps,Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps,120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.37.1 | 2.8/3.6/4 mm lens with 30 meter IR range | Each | 15056 | 56
20.37.2 | 6/8 mm Lens between 30 to 50 meter or above IR range | Each | 16559 | 556
20.37.3 | Varifocal 2.8mm to 12mm lens or better with 40 Meter IR Range or higher | Each | 24575 | 556
20.38 | SITC of IP based 8MP 4K Ultra HD Bullet camera with 1/2.8" or larger Progressive Scan CMOS Sensor with resolutions up to 3840 × 2160 (4K) @30 fps, Should Support H.264, H.265, MJPEG, Quad/Triple streaming profiles, Frame rate upto 1-30 fps, , 120dB WDR, 2DNR/3DNR, BLC. Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM. Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan.
20.38.1 | 2.8/3.6/4/6/8 mm lens with IR Range - 50mtr or higher | Each | 17483 | 556
20.38.2 | Varifocal 2.8mm to 12mm lens or better with 50 Meter IR Range or higher | Each | 26378 | 556
20.39 | SITC of 2MP (1920×1080) IR Dome PTZ with 1/ 2.8” or larger CMOS Sensor, WDR -120dB, and, PAN range 360 degree, Quad/Triple streaming profiles, Video Compression -H.265/H.264/MJPEG, IR LEDs with IR Distance of 250 mtr or more, 120dB WDR, 2DNR/3DNR, BLC.Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM it and should originate from India. Regulatory approvals include FCC, BIS/UL, CE . CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have itsservice/ support center in Rajasthan.
20.39.1 | 36x Optical Zoom and 16x or more Digital Zoom with Frame rate 30 fps | Each | 77910 | 2778
20.39.2 | 38x Optical Zoom and 16x or more Digital Zoom with Frame rate 60 fps | Each | 106807 | 2778
20.40 | SITC of 4/5 MP (minimum 2560X1440) IR Dome PTZ with minimum 36x or more Optical Zoom and minimum 16x or more Digital Zoom, 1/ 2.8” or larger CMOS Sensor, WDR -120dB, and, PAN range 360 degree, Quad/Triple streaming profiles, Frame rate upto 30 fps or more, Video Compression -H.265/H.264/M-JPEG, IR LEDs with IR Distance of 250 mtr or more, Camera should support Open standard to support ONVIF (PROFILE S, PROFILE G, PROFILE T), 1/1 Audio In/Out or better and 1/1 Alarm In/Out or better, onboard storage upto 512GB (SD card not included). The camera supports advanced Video Analytics (VA) including motion detection and alarm should be trigger on Tampering, Network disconnect, IP address conflict. CCTV should have password protection, privacy mask, IP address filtering, Metal Housing, Vandal-proof housing, IP67, IK10, DC 12V & PoE, Complete with Junction box for cable management. Operating Conditions within -20°C to 60°C or better. The MAC address of Camera/NVR must be registered in the name of OEM.Regulatory approvals include FCC, BIS/UL, CE. CCTV cameras must be BIS Registered Cyber Security Certified by STQC as per IoTSCS and meet the Essential Requirement (ER) issued by MeitY for security. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 110275 | 2778
20.41 | SITC of 8CH NVR for 2/5/8 MP cameras with minimum 1 SATA HDD Support with minimum 10 TB Capacity (minimum 10TB Capacity per slot - Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out. NVR should support minimum 80 Mbps throughput bandwidth (40 Mbps incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolutions up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 14450 | 1111
20.42 | SITC of 16CH NVR for 2/5 MP cameras with minimum 2 SATA HDD Support with minimum 20 TB Capacity (minimum 10TB Capacity per slot - Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out. NVR should support minimum 160 Mbps throughput bandwidth (80 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolutions up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE . The CCTV OEM should have its service/ support center in Rajasthan. | Each | 21281 | 1111
20.43 | SITC of 16CH NVR for 8MP Cameras with minimum 2 SATA HDD Support with minimum 20 TB Capacity (minimum 10TB Capacity per slot - Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out. NVR should support minimum 256 Mbps throughput bandwidth (128 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolutions up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps, . The system shall operate in 0°C to +50°C or better with BIS, FCC, CE .The CCTV OEM should have service/ support center in Rajasthan. | Each | 22899 | 1111
20.44 | SITC of 32CH NVR for 2/5 MP cameras with minimum 4 SATA HDD Support with minimum 40 TB Capacity (minimum 10TB Capacity per slot - Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out, Preview Capability - Upto 4K, Playback: 16-channel simultaneously. NVR should support minimum 320 Mbps throughput bandwidth (160 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolution up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps. RAID 0/1/5/10 or better. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 50515 | 2222
20.45 | SITC of 32CH NVR for 8 MP cameras with minimum 4 SATA HDD Support with minimum 64 TB capacity (Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out, Preview Capability - Upto 4K, Playback: 16-channel simultaneously. NVR should support minimum 512 Mbps throughput bandwidth (256 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolution up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps. RAID 0/1/5/10 or better. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 52584 | 2222
20.46 | SITC of 64CH NVR for 2/5 MP cameras with minimum 8 SATA HDD Support with minimum 80 TB capacity (minimum 10TB Capacity per slot - Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out, Preview Capability - Upto 4K, Playback: 16-channel simultaneously. NVR should support minimum 512 Mbps throughput bandwidth (256 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolution up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps, RAID 0/1/5/10 or better. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 80143 | 4444
20.47 | SITC of 64CH NVR for 8 MP cameras with minimum 8 SATA HDD Support with minimum 128 TB capacity (Hard Disk Not Included), minimum 1 HDMI output port, Video comression - H.265/H.264/JPEG, 1/1 Audio In/Out, Preview Capability - Upto 4K, Playback: 16-channel simultaneously. NVR should support minimum 1024 Mbps throughput bandwidth (512 incoming bandwidth), ONVIF compliance (Profile S/G/T). Recording resolution up to 4K/8MP, minimum 2 USB Ports, minimum 1 Ethernet Ports (RJ-45) 10/100/1000Mbps, RAID 0/1/5/10 or better. The system shall operate in 0°C to +50°C or better with BIS, FCC, CE. The CCTV OEM should have its service/ support center in Rajasthan. | Each | 84720 | 4444
20.48 | SITC of 3.5" 4TB internal HDD for cctv recording ,capable for 24x7 operation, hdd rpm capacity shoud be 7200 rpm or better, Buffer should be 512 MB as required of following size.
20.48.1 | 4 TB | Each | 13923 | 222
20.48.2 | 6 TB | Each | 17900 | 222
20.48.3 | 8 TB | Each | 21413 | 222
20.48.4 | 10 TB | Each | 25720 | 222
20.48.5 | 12 TB | Each | 31386 | 222
20.49 | SITC of following diagonal size professional Display, 4k Resolution, Brightness(Typ.) 440 nit and above , Contrast Ratio-2000:1 and above, Viewing Angle(H/V)-178/178, Response Time(G-to-G) 8ms, Input: RGB- Analog D-SUB, Video- HDMI 2.0 (2), HDCP- HDCP 2.2, Audio- Stereo mini Jack, USB- Only F/W upgrade, Outputs: RGB- DP1.2(Loop- out), Audio- Stereo mini Jack, External Control- RS232C(in/out), RJ45, External Sensor Detachable type(IR Ambient). Operation Hour 24/7. mounting bracket etc. as required.
20.49.1 | 32" | Each | 32342 | 556
20.49.2 | 43" | Each | 43901 | 556
20.49.3 | 55" | Each | 57749 | 1111
20.49.4 | 65" | Each | 88913 | 2222
20.49.5 | 75" | Each | 146708 | 2222
IPBX
20.50 | SITC of IP-PBX which is IP at its core and act as a Unified Communication System with IP switching technology and 100% non-blocking, configured for below mentioned. The system should be IPV6 ready, should have VoIP and Voice mail at its core i.e. these modules should be mountable on the CPU. The system should be Q Sig Ready, inbuilt Auto-attendant facility, Returned Call to Original Caller (RCOC), CLI based DISA (Mobile Extension)System, Should support SNMP manager for managing and monitor network elements, audit network usage and detect network faults, should support SIP over TLS and SRTP, minimum 2 Gigabit Ethernet ports for LAN and WAN, built-in multi-party conferencing facility with 21 party in a single conference, minimum one RS232 ports for SMDR/PMS/CAS Interface. The System have have capability to also act like Universal Media Gateway when required. The System should have facility of Conversation recording on Analog/Digital/IP ports as well as on Mobile SIP Smartphones, UC Client application for Android, iPhone and on Windows PC. Power supply should be inbuilt and SMPS type with input ranges from 100 – 240 V AC, 47-60 Hz OR 48VDC +/- 15%. The system must have Certification: TEC, CE, FCC, ROHS.
20.50.1 | 48 analogue extensions, 04 PSTN Trunk Port, 12 Channel SIP PRI, 04 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 224 TDM ports and minimum 500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 177827 | 4444
20.50.2 | 64 analogue extensions, 08 PSTN Trunk Port, 16 Channel SIP PRI, 08 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 224 TDM ports and minimum 500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 226284 | 6666
20.50.3 | 96 analogue extensions, 08 PSTN Trunk Port, 30 Channel SIP PRI, 08 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 224 TDM ports and minimum 500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 273181 | 8888
20.50.4 | 128 analogue extensions, 08 PSTN Trunk Port, 30 Channel SIP PRI, 08 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 224 TDM ports and minimum 500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 303144 | 11110
20.50.5 | 192 analogue extensions, 08 PSTN Trunk Port, 30 Channel SIP PRI, 08 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 224 TDM ports and minimum 500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 371714 | 13332
20.50.6 | 256 analogue extensions, 08 PSTN Trunk Port, 30 Channel SIP PRI, 08 Digital Port, 15 IP User License, 5 IP Softphone/mobile user license, 08 VoIP Channel License along with 8 port Voice Mail expandable upto minimum 512 TDM ports and minimum 1500 SIP/IP users without any add-on CPU or chassis/hardware platform. | Each | 773603 | 22220
20.51 | SITC of Line Card for required Analog / Digital / CO Extensions. compatible to the IP PBX as required.
20.51.1 | 16 Analogue Extensions | Each | 34828 | 556
20.51.2 | 8 CO Extensions | Each | 26390 | 556
20.51.3 | 8 Digital Extensions | Each | 31132 | 556
20.51.4 | CLI based Telephone Instrument, with Caller ID, 2 way /Hands free speaker, 16 Digit LCD Display, Adj. volume | Each | 1450 | 111
20.52 | SITC of Digital Phone/Operator Console with 240 x 64 or better– Pixel Graphical LCD with Backlit, LED for Incoming/Ongoing Call, Mute, Call Hold, Do Not Disturb, Speed Dial, Hotline, Redial, Call Back, Auto Answer, Call Forward, Call Waiting, Call Transfer, Room Monitoring, Conference, Directory, Call Logs ,Dial-by-Name, Message wait Lamp, Ringer Lamp. Voice Mail ,Call Pickup – Group and Selective, backlight display panel, minimum 16 memory/speed dial keys can be extended upto 128 keys with support of Add on key module, 4 Context Sensitive Hard Keys, Multiple Languages, Caller ID with Name & Number, RJ9 Handset Port, 3.5 mm Headset Port, Certifications - TEC, CE, FCC, RoHS. | Each | 11478 | 333
20.53 | SITC of Type-I IP Phone with 128 x 64 or better –pixel Graphical LCD , Extended SIP Protocol, LED for Call and message wait Indication, 3 Feature Keys:Headset, Mute, Hands-free speaker phone, 4 Context Sensitive Keys, 2 Line keys with Function such as navigation, Call Appearance , feature status, Volume Control Keys, 2 X RJ45 10/100/1000 Mbps Ethernet Ports, Power Over Ethernet (IEEE 802.3af), minimum one RJ9 Handset port, one RJ9 Headset port & Power Supply - 5VDC 0.6A, Power consumption - 1Watt, 0°C to 45°C or better, Certifications: TEC, CE, FCC, RoHS. | Each | 6422 | 111
20.54 | SITC of Type-II IP Phone with 240 x 64 or better – Graphical LCD with Backlit, minimum 2 x 10/100/1000 Mbps LAN & PC Ports, LED for Incoming/Ongoing Call, Mute, Call Hold, Do Not Disturb, Speed Dial, Hotline, Redial, Call Back, Auto Answer, Call Forward, Call Waiting, Call Transfer, Dial-by-Name, Message wait Lamp, Ringer Lamp. Voice Mail ,Call Pickup – Group and Selective, backlight display panel, 16 memory/speed dial keys can be extended upto 128 keys with support of Add on key module, 4 Context Sensitive Hard Keys, Multiple Languages, Caller ID with Name & Number, RJ9 Handset Port, 3.5 mm Headset Port, Power consumption - 5Watt, Power Supply - 5VDC/600mA, 0°C to 45°C or better, Certifications - TEC, CE, FCC, RoHS. | Each | 10138 | 556
20.55 | SITC of IP Video Phone for Android Platform with 16-line/16 SIP accounts with a multi-platform video conferencing solution and the functionality of an Android tablet to offer an all-in-one communications solution. The phone features a 8” (1280x800) capacitive touch screen IPS LCD, 2 Mega pixel camera, Quad-core 2.0GHz ARM Cortex-A55 processor with 4GB RAM and 16GB, eMMC Flashdual microphone, dual Gigabit ports with PoE/PoE+, 12-way audio conferencing & 3-way 1080p 30fps HD video conferencing capability, integrated Wi-Fi 6 (802.11 a/b/g/n/ac/ax) & Bluetooth 5.0, rich peripheral interfaces. It also runs on Android 14 operating syatem and offers instant access to thousands of Android apps. Certification: CE, FCC, RoHS. | Each | 45566 | 1111
20.56 | SITC of Pure IP-PBX which is IP at its core with IP switching technology and is having pure IP Architecture with embedded hardware platform, configured for 180 IP Extension, 04 PSTN Trunk Port, 30 Channel SIP PRI, 5 IP Softphone/mobile user license, 64 VoIP Channel License along with 4 port Voice Mail expandable upto 2000 IP Extensions without any add-on CPU/hardware platform. System should have provision to connect any TDM trunk and FXS extensions i.e. CO, PRI, GSM, Radio with external VoIP Gateway from same OEM. The system should support at least 21 concurrent Call Tapping and Conversation Recording, 64 Participants Audio Conference, 21 Three-party Conference Provision. The system should be IPV4 & IPV6 ready, should have VoIP and Voice mail at its core,The system should support SIP/IP extensions and SIP Trunks with the single VoIP module over SIP Protocol. The system architecture should be non-stackable eliminating individual power supply for each chassis. The system should have inbuilt Auto-attendant facility with multi lingual IVR, Corporate Directory Integration, Unified messaging, Returned Call to Original Caller (RCOC), CLI based DISA System, minimum 2 Gigabit Ethernet ports for LAN and WAN to separate out local and VoIP traffic on the external network. The system should have adapter based power supply with output of 24V DC, 2.5A. It should have dual power supply port for Hot redundancy. Certification: TEC, CE, FCC, ROHS. | Each | 125080 | 11110
20.57 | SITC of IP user license for 10 User with required VOIP Channels. compatible to the IP PBX being used. | Each | 10081 | 222
20.58 | SITC of Daughter-board Module for VoIP Channels and IP user license. compatible to the existing IP PBX being used. | Each | 14218 | 222
20.59 | SITC of VoIP-FXS-FXO Gateway configured for required FXS(Analog) / FXO(CO) ports, VoIP Channels with SIP Accounts, minimum 1 Ethernet Port for network connectivity. It shall employ IP/PCM/TDM, 100% non-blocking, Digital-IP switching technology. It should have Password Protected Web based UI, TR069 for Mass Management, SNMP for Mass Monitoring, PCAP Trade. The Gateway device should have Peer-to-peer dialing facility with table entries. The Gateway device must have interoperability with different service providers. The Gateway should be available with Power supply/Power Adaptor of 24VDC, 2.5 A with maximum 60W power Consumption. Certification: TEC, CE, FCC, RoHS.
20.59.1 | 32 FXS / Analog ports, 32 VoIP Channels with 32 SIP Accounts | Each | 53542 | 1111
20.59.2 | 16 FXS / Analog ports, 32 VoIP Channels with 32 SIP Accounts | Each | 36597 | 1111
20.59.3 | 04 FXO / CO ports, 04 VoIP Channels with 08 SIP Accounts | Each | 15086 | 1111
20.60 | Supply, Installation, Testing & Commissioning of Chairman Unit with fixed microphone and flexible stem prority button for chairman microphone ,optioal chime tone facility for proceeding chairman announcement with two headphone socket built in loudspeaker is automatcally muted when the microphone is on/off button chairman mike unit should have a frequency responce 400hz to10hz ,length of microphone from base to steam should not be less than 488 mm in size ;nominal acoustic input 85 db SPL,dimensions (without microphone) (HxWxD) 50x135x135 mm; weight of unit should not be less then 1.2 kg ;operating temperature -5°C to +45°C,two 3.5mm (0.14 in) stereo headphone sockets; including make connecion testing etc complete as required. | Each | 16204 | 600
20.61 | supply, Installation, Testing & Commissioning of Delegate mike Unit with fixed microphone and flexible stem prority button for Deligate mike microphone ,optioal chime tone facility for proceeding Delegate mike announcement with two headphone socket built in loudspeaker is automatcally muted when the microphone is on/off button Delegate mike unit should have a frequency responce 400hz to10hz ,length of microphone from base to steam should not be less than 488 mm in size ;nominal acoustic input 85 db SPL,dimensions (without microphone) (HxWxD) 50x135x135 mm; weight of unit should not be less then 1.2 kg ;operating temperature -5°C to +45°C,two 3.5mm (0.14 in) stereo headphone sockets; including make connecion testing etc complete as required. | Each | 15004 | 556
20.62 | Supply, Installation, Testing & Commissioning of Control Unit for giving power to chairman unit asd delegate unit with inbulit 3 band equlilzer unit comprrising of knobs at 250hz, 2khz and 8khz volume control for 1 mic input 8 pin din connector for loop through should also consists microphone input with xlr connector with rated output impedance of 1000ohm and systems should have capability to control up 50 dicussion unit,unit dimensions should not be less then (85mm x 360mm x 250 mm) in size; including make connection testing etc complete as required. | Each | 36010 | 1333
20.63 | SITC of 30 Watt speaker with taping facility having frequency range of 65Hz-20KHz@(-10db) with power handing of 200Watt continuous and more than 350 Watt @peak etc complete as required. | Each | 19805 | 733
20.64 | Supply & Installation of 240 Watt Mixer Amplifier Unit- for providing a crisp call or clear music with 4 microphone / line inputs, plus music source input, announcement only output, 3 wire volume override, with Mains power supply 230 VAC ±10%, 50 Hz (reduced power at lower mains), Inrush current 20 A , Power consumption 120W, Frequency response (Line) 80 Hz to 18 kHz (+1/‑3 dB @‑10 dB ref. rated output) Frequency response (Mic.) 80 Hz to 18 kHz (+1/‑3 dB @‑10 dB ref. rated output) Distortion <1%@ rated output power, 1 kHz Bass Control Max. ± 8 dB Treble Control Max. ± 8 dB, including making connection etc complete as required. | Each | 31208 | 1155
20.65 | Supply& laying of 8 core shielded cable for extension cable for contribution unit /control unit interconnection making connection testing etc complete as required. | Each | 372 | 14
20.66 | Supply & Laying of 2 Core size 0.5 sqmm copper shielded Cable for connectings Microphones with related conduits / fittings / termination, etc complete as required. | Each | 42 | 2
20.67 | Supply, Installation, Testing & Commissioning of 2 input 4 output hdmi splitter complete as required. | Each | 6002 | 222
20.68 | Supply, Installation, Testing & Commissioning of High−performance 15 meter HDMI male to HDMI male cable Wall plate for the interoperability in all respect to etc complete as required. | Each | 3021 | 116
20.69 | SITC of BIS approved Line Interactive UPS having 0.6 Output factor, Built In AVR & SMF Batteries. Input Voltage range of 160V-280V, 1 Phase; 50 Hz and Output voltage of 230V±10%; 50Hz±1Hz. UPS should have Under / Over voltage, Spike, Overload, Short circuit protection and give audible alarm during Battery mode, Low battery, Overload, Fault conditions. UPS should be Genset compatible,shall have auto resart & cold start feature and Indian type output sockets. etc. as required.
20.69.1 | 600VA LI UPS with 84 VAH Battery | Each | 5655 | 555.5
20.69.2 | 1000VA LI UPS with 168 VAH Battery | Each | 11888 | 556
20.70 | SITC of following capacity BIS certified 1Phase Input, 1Phase Output advance DSP controlled IGBT based rectifier Online UPS with 0.99 Input power factor &0.8 Output factor, having Input voltage & frequency range of 180-300V on full load/ 110-300V on 60% load & 50 Hz +/- 5% and output voltage & frequency of 230V+/-1% & 50 +/- 0.1 Hz.Overloading of 105 - 110% 10 mins, 111 - 130% 2 mins,131 - 150% 30 sec, THDv of < 3% for Linear & < 5% for Non linear load.UPS should have LCD display showing load level, Battery Voltage Level, Input & Output Voltage, Input & Output Frequency. UPS should have protection from Input High / Low;Over Load;Short Circuit; Over Temperature and give audible alarms on Battery Mode;Low Battery;Fault;Over Load & Bypass Mode.SMF Batteries of 12V VRLA for 30 min back up with MS Rack and necessary cable for UPS to Batteries Installation. UPS should have CE, ROHS, IEC62040-1,2&3 compliance and should have QR code which should contain drawing, test report OEM manual,Geo- Tag of manufacturing location Etc. as required.
20.70.1 | 1KVA UPS with 936 VAH Battery | Each | 51959 | 556
20.70.2 | 2KVA UPS with 1872 VAH Battery | Each | 82771 | 1111
20.70.3 | 3KVA UPS with 3024 VAH Battery | Each | 101725 | 1111
20.71 | SITC of following capacity BIS certified 1Phase Input, 1Phase Output advance DSP controlled IGBT based rectifier Online UPS with Inbuilt Isolation Transformer having 0.99 Input power factor & 0.8 Output factor, Input voltage & frequency range of 180-300V on full load/ 110-300V on 50% load & 50 Hz +/- 5% and output voltage & frequency of 230V+/-1% & 50 +/- 0.1 Hz. Overall efficiency of upto 92% (without Transformer Loss), Overloading of 105 - 110% 30 mins, 111 - 130% 5 mins,131 - 150% 10 sec, THDv of < 3% for Linear & < 5% for Non linear load.UPS should have LED Panel with LCD display showing load level, Battery Voltage Level, Input & Output Voltage, Input & Output Frequency. UPS should have protection from Input High / Low;Over Load;Short Circuit; Over Temperature and give audible alarms on Battery Mode;Low Battery;Fault;Over Load & Bypass Mode. SMF Batteries of 12V VRLA for 30 mins with MS Rack and necessary cable for UPS to Batteries Installation. UPS should have valid Certification like Type III environmental declarations from third party renowned agency complying to ISO 14025, CE, ROHS,BIS,EN 62040-1, EN 62040-2, IEC 62040-3 Etc. as required.
20.71.1 | 5KVA UPS with 4992 VAH Battery | Each | 218293.0574 | 1111
20.71.2 | 10KVA UPS with 9072 VAH Battery | Each | 315661 | 2222
20.72 | SITC of following capacity BIS certified (if applicable) 3Phase Input, 1Phase Output Online double conversion VFI-SS-111 IGBT based UPS (Rack/Tower 3U) with 0.99 Input power factor & unity Output factor(KVA=KW), having Input side Internal / External Isolation Transformer, voltage & frequency range of 305-485V & 40-70 Hz and output voltage & frequency of 230V+/-1% & 50 +/- 0.1 Hz.UPS should have EPO,dust filter & conformal coated boards, Overall efficiency of upto 96% at rated voltage & frequency, Overloading of < 105% continious,106-110% 60 mins, 111 - 130% 10 mins,131 - 155% 1 min, THDv of < 1% for Linear & < 3% for Non linear load.UPS should have LED Panel with Auto rotating LCD display showing real time UPS status with other parameters like Input, Output, Bypass - Voltage/ Frequency/Current, Output -VA/W/power factor/load percentage, Battery -Voltage/ Current/Status of charge/Remaining backup time percentage/ Self test.UPS should have protection from Input High / Low; Over Load;Short Circuit; Over Temperature and give audible alarms on Battery Mode;Low Battery;Fault;Over Load & Bypass Mode.UPS Monitoring through communication port RS 485. SMF Batteries for 30 min back up with MS Rack and necessary cable for UPS to Batteries Installation. UPS should have CE, ROHS, IEC62040-1,2&3 compliance and should have QR code which should contain drawing, test report OEM manual,Geo- Tag of manufacturing location Etc. as required.
20.72.1 | 10KVA (3/1) UPS with 9072 VAH Battery | Each | 345521 | 5555
20.72.2 | 15KVA (3/1) UPS with 13056 VAH Battery | Each | 598368 | 5555
20.73 | SITC of 3Phase Input, 3Phase Output Online double conversion VFI-SS-111 IGBT based Rectifier & Inverter UPS with 0.99 Input power factor & unity Output factor(KVA=KW), having Inbuilt Isolation Transformer at Input, Phase balance of 120° ±1° (100% unbalanced load), input voltage & frequency range of 320-480V & 45-55 Hz and output voltage of 415V (+/- 1% for balanced & +/- 2% for unbalanced load) & output frequency of 50Hz +/- 0.1 Hz.UPS should have Inbuilt phase sequence corrector & protector both (UPS should correct the Input Phase reversal condition & shall not go to battery mode) and Input, output & Bypass breaker, UPS should have Inbuilt Static & maintenance bypass, Parallel kit, EPO, dust filter & conformal coated boards, Overall efficiency without transformer loss (93% for 10KVA, 94% for 20KVA & 30KVA, 95% for 40KVA& 60KVA) , Overloading on mains mode </= 110% for 60 mins, </= 125% for 10 mins, </=150% for 1 min, THDi < 4%. UPS should have LED Panel with minimum 5 inch Intuitive Touch Screen LCD Displayy showing UPS status with other parameters like Input, Output, Bypass - Voltage/ Frequency,load%, Battery%. UPS should have protection from Input High / Low; Over Load;Short Circuit; Over Temperature and give audible alarms on Battery Mode;Low Battery;Fault;Over Load & Bypass Mode.UPS communication through RS485. SMF Batteries of 12V VRLA for 30 min back up with MS Rack having battery breaker with enclosure and necessary cable for UPS to Batteries Installation of 20 Mtrs.UPS should have feature to connect similer model & capacity with common battery bank.Operating Temperature of UPS 40 degree, relative humidity 0-95% (Non condensing), Noise level of 65dBA @1 mtr. UPS should have CE, ROHS, IEC62040-1,2&3 compliance and should have QR code which should contain drawing, test report OEM manual, Geo- Tag of manufacturing location Etc. as required.
20.73.1 | 10KVA UPS with 10080 VAH Battery | Each | 561218 | 8333
20.73.2 | 20KVA UPS with 20160 VAH Battery | Each | 809486 | 5555
20.73.3 | 30KVA UPS with 31200 VAH Battery | Each | 1003331 | 11110
20.74 | SITC of 1Phase Input, 1Phase Output Microprocessor control based Inverter with input voltage range of 180-260V and output voltage same as input 210V +/- 10%, output frequency of 50 +/- 0.1 Hz and 0.8 Output factor. Overall efficiency of upto 80%, Transfer time 15 msec & Sinewave output.Inverter should have LED/LCD Panel Display showing Mains ON, INV. ON, Charging/Charged.Inverter should have protection from Overload/Short Circuit Trip/Over Temperature and Low Battery Trip.Batteries should be Tubular Type for 60 min back up with Trolley/Rack and necessary cable for Inverter to Batteries Installation.
20.74.1 | 1KVA (1/1) Inverter with 1600 VAH | Each | 30041 | 16665
20.74.2 | 2KVA (1/1) Inverter with 3200 VAH | Each | 58927 | 578
20.74.3 | 3KVA (1/1) Inverter with 4800 VAH | Each | 87351 | 1133
20.74.4 | 5KVA (1/1) Inverter with 8000 VAH | Each | 155984 | 1680
20.75 | S & F of 12V VRLA Lead Acid Sealed maintenance free (SMF) batteries of following capacity with Warranty of 2 years
20.75.1 | 7.0 AH | Each | 1267 | 3000
20.75.2 | 9 AH | Each | 1698 | 111
20.75.3 | 12 AH | Each | 2378 | 111
20.75.4 | 18 AH | Each | 2967 | 111
20.75.5 | 26 AH | Each | 3341 | 111
20.75.6 | 28 AH | Each | 3511 | 111
20.75.7 | 34 AH | Each | 4689 | 111
20.75.8 | 42 AH | Each | 4871 | 111
20.75.9 | 65 AH | Each | 6739 | 111
20.75.10 | 100 AH | Each | 10128 | 167
20.75.11 | 120 AH | Each | 13708 | 222
20.75.12 | 150 AH | Each | 15940 | 222
20.76 | Replacement of Existing Battery with 12V VRLA Lead Acid Sealed maintenance free (SMF) batteries of following capacity with Warranty of 2 years (The old battery shall be retained by contractor)
20.76.1 | 12V 7 AH | Each | 1151 | 111
20.76.2 | 12V 9 AH | Each | 1539 | 111
20.76.3 | 12V 12 AH | Each | 2151 | 111
20.76.4 | 12V 18 AH | Each | 2681 | 111
20.76.5 | 12V 26 AH | Each | 3018 | 111
20.76.6 | 12V 28 AH | Each | 3171 | 111
20.76.7 | 12V 34 AH | Each | 4232 | 111
20.76.8 | 12V 42 AH | Each | 4395 | 111
20.76.9 | 12V 65 AH | Each | 6082 | 167
20.76.10 | 12V 100 AH | Each | 9132 | 167
20.76.11 | 12V 120 AH | Each | 12303 | 167
20.76.12 | 12V 150 AH | Each | 14368 | 167
20.76.13 | 12V 185 AH | Each | 18503 | 222
Note
1 | To ensure the health of the network, it is mandatory to conduct Penta Scanning of the network having I/O (Information Outlets) more than 150 nos.
2 | As per NEC 2023, voltage level are classified as under: ELV: Un≤ 50 V AC, Un≤120 V DC. LV : Un≤ 1000 V AC, Un≤1500 V DC. MV : 1 KV < Un≤ 33 KV AC. HV : 33 KV < Un≤ 150 KV AC.

## ch 21 Pumps
Chapter E - 21
Electrical Driven Pumpsets
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
21.1 | Labour charges for installation of submersible motor pump set including lowering/ delowering of pipes, cables, accessories etc. in tube-well/ open well complete including T&P, transportation of tripod, chain pulley block & any other material required for this purpose complete in all respect.
21.1.1 | Lowering only | Job |  | 3626
21.1.2 | Delowering only | Job |  | 2946
21.1.3 | Delowering and Lowering | Job |  | 5893
21.2 | Supply & fixing of PVC threaded casing pipes for Tube well (IS 12818:1992) as required
21.2.1 | Up to 400 ft Depth
21.2.1.1 | 150 mm dia | Mtr. | 650 | 83
21.2.1.2 | 175mm dia | Mtr. | 893 | 100
21.2.1.3 | 200 mm dia | Mtr. | 1164 | 144
21.2.1.4 | 250 mm dia | Mtr. | 1708 | 178
21.2.2 | more than 400 ft to 1200 ft. Depth
21.2.2.1 | 40mm dia | Mtr. | 124 | 33
21.2.2.2 | 50 mm dia | Mtr. | 186 | 44
21.2.2.3 | 80mm dia | Mtr. | 254 | 67
21.2.2.4 | 100 mm dia | Mtr. | 338 | 83
21.2.2.5 | 125 mm dia | Mtr. | 508 | 111
21.2.2.6 | 150 mm dia | Mtr. | 694 | 128
21.2.2.7 | 175 mm dia | Mtr. | 938 | 144
21.2.2.8 | 200 mm dia | Mtr. | 1242 | 222
21.2.2.9 | 250 mm dia | Mtr. | 1774 | 244
21.3 | Providing & Laying of Polypropylene rope Confirming to IS:5175 for submersible pump of following sizes. complete in all respect.
21.3.1 | 12mm (suitable up to 50 mm OD pipe) | Mtr. | 40 | 3
21.3.2 | 16mm (suitable above 50mm & up to 75 mm OD pipe) | Mtr. | 49 | 3
21.3.3 | 20mm (suitable for 90 mm OD pipe) | Mtr. | 57 | 3
21.4 | Providing & Fixing of HDPE pipe Confirming to IS:4984:2021 for water supply suitable for submersible & jet pump with required fittings ie socket, elbows, tee etc. complete in all respect.
21.4.1 | for vertical installation
21.4.1.1 | 40 mm OD 6 kg / cm2 | Mtr. | 78 | 12
21.4.1.2 | 50 mm OD 6 kg / cm2 | Mtr. | 103 | 12
21.4.1.3 | 63 mm OD 6 kg / cm2 | Mtr. | 149 | 13
21.4.1.4 | 75 mm OD 6 kg / cm2 | Mtr. | 194 | 24
21.4.1.5 | 90 mm OD 10 kg / cm2 | Mtr. | 320 | 31
21.4.2 | for Horizontal installation
21.4.2.1 | 40 mm OD 4kg/ cm2 | Mtr. | 71 | 12
21.4.2.2 | 50 mm OD 4 kg/ cm2 | Mtr. | 98.3 | 13
21.4.2.3 | 63 mm OD 4 kg/ cm2 | Mtr. | 144 | 19
21.4.2.4 | 75 mm OD 4 kg/ cm2 | Mtr. | 172 | 24
21.4.2.5 | 90 mm OD 6 kg/ cm2 | Mtr. | 286 | 31
21.5 | SITC of Single Stage, water cooled, High Speed (2880 RPM), Horizontal, Centrifugal, Openwell Submersible pumps set pre filled with coolent water and fitted with mechanical seal. The motor body of single phase pump shall be of SS and rest of all shall be of cast iron. Shaft of three phase pump shall be of SS 410 grade. All casting parts should be cathod electro deposition (CED) coated. Motor winding shall be 100% copper wire material. Dynamically balanced rotating parts to ensure min. vibration etc. All labour for testing of submersible pumps set and supply of water to water mains, complete in all respect.
21.5.1 | 0.5 HP, 1-Ø, (7 -18) Mtr, (180 - 20) LPM | Each | 10144 | 889
21.5.2 | 1.0 HP, 1-Ø, (12 -27) Mtr, (200- 30) LPM | Each | 12755 | 1111
21.5.3 | 1.5 HP, 1-Ø, (18 -33) Mtr, (160-35) LPM | Each | 18587 | 1333
21.5.4 | 2.0 HP, 1-Ø, (9 -21) Mtr, (475 - 130) LPM | Each | 20966 | 1333
21.5.5 | 3.0 HP, 3-Ø, (17 -27) Mtr, (680 - 250) LPM | Each | 23710 | 1555
21.5.6 | 5.0 HP, 3-Ø, (13 -36) Mtr, (995-200) LPM | Each | 26717 | 1778
21.5.7 | 7.5 HP, 3-Ø, (12 -32) Mtr, (1650-400) LPM | Each | 30625 | 2222
21.5.8 | 10.0 HP, 3-Ø, (15 -36) Mtr, (1860 - 700) LPM | Each | 45946 | 2778
21.5.9 | 12.5 HP, 3-Ø, (19.5 -33) Mtr, (2150-1300) LPM | Each | 54865 | 3333
21.5.10 | 15.0 HP, 3-Ø, (16 -36) Mtr, (2300-1250) LPM | Each | 67865 | 3555.2
21.6 | SITC of Radial / mixed flow water and anti-corrosive liquid filled submersible motor pump sets suitable for 100/150mm dia borewell. The size of adopter fixed on top of the motor should exceed the top of coupler , for safegaurd the coupler. The job includes labour part of lowering of riser pipe G.I./ H.D.P.E. with rope, cables & pump, installation of complete fitting and accessories, jointing of electrical cables up to Starter. All labour for testing of submersible pumps set and supply of water to water mains, complete in all respect.
21.6.1 | 100 mm diameter Submersible pump shall have following HP Rating, phase, Head range, Discharge range respectively.
21.6.1.1 | 1.0 HP, 1-Ø, (10 - 83)Mtr, (40- 10) LPM | Each | 19987 | 3555
21.6.1.2 | 1.5HP, 1-Ø, (11 - 94)Mtr, (40 - 10) LPM | Each | 22364 | 3666
21.6.1.3 | 2.0 HP, 1-Ø, (7- 95)Mtr, (55-22) LPM | Each | 24118 | 3833
21.6.1.4 | 3.0 HP, 1-Ø, (40 -170)Mtr, (60- 20) LPM Copper Wound | Each | 36523 | 4000
21.6.1.5 | 5.0 HP, 1-Ø, (56 - 236)Mtr, (90 - 25) LPM Copper wound | Each | 46940 | 4444
21.6.2 | 150 mm diameter Submersible pump shall have following HP Rating, phase, Head range, Discharge range respectively.
21.6.2.1 | 3.0 HP, 3-Ø, (40 -110)Mtr, (280-50) LPM | Each | 40798 | 4000
21.6.2.2 | 5.0 HP, 3-Ø, (72 - 161)Mtr, (230-48) LPM | Each | 48333 | 4000
21.6.2.3 | 7.5 HP, 3-Ø, (85-165)Mtr, (300-100) LPM | Each | 52195 | 44440
21.6.2.4 | 10.0 HP, 3-Ø, (110 - 212)Mtr, (400-167) LPM | Each | 69837 | 6110
21.6.2.5 | 12.5 HP, 3-Ø, (129 - 250)Mtr, (400-163) LPM | Each | 77659 | 6110
21.6.2.6 | 15.0 HP, 3-Ø, (150 - 280)Mtr, (400-167) LPM | Each | 81470 | 6110
21.7 | SITC of Monoblock closed coupled motor pump set with TEFC motor, motor should be IP55-F class and IE2 efficiency for monobloc, with carbon steel /SS-410 shaft, Mechanical seal, Single/Three phase Including cost of hardware etc on existing platform complete. Pump shall have following HP Rating, phase, Head, minimum Discharge respectively and Dynamically balanced rotating parts to ensure min. vibration etc. complete in all respect.
21.7.1 | 0.5 HP, 1-Ø, (8 - 26)Mtr, (50-10) LPM (SS Impellor & SS Body) | Each | 6899 | 667
21.7.2 | 0.5 HP, 1-Ø, (8 - 26)Mtr, (50-10) LPM ( Bronze impeller & CI Body) | Each | 10310 | 667
21.7.3 | 1.0 HP, 1-Ø, (10-30)Mtr, (76-28) LPM ( Bronze impeller & Aluminium Body) | Each | 7801 | 889
21.7.4 | 1.0 HP, 1-Ø, (10-30)Mtr, (76-28) LPM ( Bronze impeller & CI Body) | Each | 13660 | 889
21.7.5 | 1.5 HP, 1-Ø, (15-40)Mtr, (78-15) LPM ( Bronze impeller & CI Body) | Each | 15186 | 1111
21.7.6 | 2.0 HP, 1-Ø, (6-27)Mtr, (250-100) LPM ( Bronze impeller & CI Body) | Each | 17363 | 1333
21.7.7 | 2.0 HP, 3-Ø, (6-27)Mtr, (250-100) LPM ( Bronze impeller & CI Body) | Each | 22184 | 1333
21.7.8 | 3.0 HP, 3-Ø, (12 - 26)Mtr, (470-275) LPM ( Bronze impeller & CI Body) | Each | 29093 | 1555
21.7.9 | 5.0 HP, 3-Ø, (19-44)Mtr, (550-300) LPM ( Bronze impeller & CI Body) | Each | 33055 | 1778
21.7.10 | 7.5 HP, 3-Ø, (20-35)Mtr, (1060-400) LPM ( Bronze impeller & CI Body) | Each | 42225 | 2222
21.7.11 | 10.0 HP, 3-Ø, (16- 48)Mtr, (850-450) LPM ( Bronze impeller & CI Body) | Each | 495582 | 2666
21.7.12 | 12.5 HP, 3-Ø, (20- 64)Mtr, (886-490) LPM,( Bronze impeller & CI Body) | Each | 67791 | 4444
21.7.13 | 15.0 HP, 3-Ø, (18- 70)Mtr, (900-450) LPM , ( Bronze impeller & CI Body) | Each | 75610 | 4444
21.7.14 | 20.0 HP, 3-Ø, (48- 59)Mtr, (800-480) LPM, ( Bronze impeller & CI Body) | Each | 32133 | 5555
21.7.15 | 25.0 HP, 3-Ø, (42- 56)Mtr, (1700-950) LPM, ( Bronze impeller & CI Body) | Each | 130187 | 6666
21.7.16 | 30.0 HP, 3-Ø, (42- 65)Mtr, (1840-1280) LPM, ( Bronze impeller & CI Body) | Each | 170190 | 6666
21.8 | SITC of Dewatering Submersible Motor Pump set, motor should be IP68/F class/IE3class suitable to handle raw sewage suitable for Minimum 25 mm solid and CI Impellor, CI body & housing ( as per IS-210 standard) and SS shaft, Double mechanical seal etc. as required. Pump shall have following HP Rating, phase, Head, minimum Discharge respectively 10 Mtr cable length etc. complete in all respect. The submersible pumpset shall be suspended with chain for ease of connection and disconnection from discharge pipe assembly.
21.8.1 | 1.0 HP, 3-Ø, (5 - 10)Mtr, (350 - 50) LPM | Each | 29216 | 1111
21.8.2 | 2.0 HP, 3-Ø, (8 - 15)Mtr, (480 - 50) LPM | Each | 37690 | 1778
21.8.3 | 3.0 HP, 3-Ø, (8 - 18)Mtr, (800 - 76) LPM | Each | 52973 | 2222
21.8.4 | 5.0 HP, 3-Ø, (10 - 20)Mtr, (940 - 75) LPM | Each | 74876 | 2778
21.8.5 | 7.5 HP, 3-Ø, (7 - 25)Mtr, (1400 - 250) LPM | Each | 119301 | 2778
21.9 | SITC of Drain Sewage pump Non-clog, Semi-open, single vane with alloy cutter fully floodable submersible pump motor should be IP68/F class/IE3, suitable to handle raw sewage suitable for Minimum 25 mm solid with CI Impellor, CI body & housing, SS shaft, Double Mechanical seal etc. as required. Pump shall have following HP Rating, phase, Head, minimum Discharge respectively, 10 Mtr cable length etc. complete in all respect. The submersible pumpset shall be suspended with chain for ease of connection and disconnection from discharge pipe assembly.
21.9.1 | 1.0 HP, 3-Ø, (4 - 12)Mtr, (400 - 45) LPM | Each | 33230.9877 | 1111
21.9.2 | 2.0 HP, 3-Ø, (8 - 16)Mtr, (375 - 40) LPM | Each | 42820 | 1778
21.9.3 | 3.0 HP, 3-Ø, (8 - 22)Mtr, (590 - 80) LPM | Each | 56340 | 2222
21.10. | SITC of Pressure boosting pump with MS Tank, pressure switch, pressure gauge, and all standard fittings fully automatic ON / OFF system, 2900 RPM with stainless steel casing, & impellor suitable for following capacity complete in all respect.
21.10.1 | 0.5 HP ( 12 - 26 ) Mtr, (50 - 10 ) with 8 Ltr tank | Each | 22760 | 889
21.10.2 | 0.75 HP -0.90 HP ( 10 - 34 ) Mtr, (72 - 5 ) LPM with 24 Ltr Tank | Each | 25551 | 1111
21.10.3 | 1.0 HP ( 10 - 38 ) Mtr, (76 - 8 ) LPM with 24 Ltr Tank | Each | 28895 | 1111
21.10.4 | 1.5 HP ( 18-44 ) Mtr, (10-78 ) LPM with 35 ltr tank | Each | 37667 | 1333
21.11 | Providing & Fixing of CI foot valve complete in all respect as required.
21.11.1 | 50/ 60 mm | Each | 1219 | 200
21.11.2 | 80/ 100 mm | Each | 2438 | 400
21.12 | Supply & fixing of GI pipes confirming to IS : 1239 P - 1 ( 2004 ) with socket,elbow,tee, flanges duly screwed & welded including rubber washer, nuts & bolts of 8mm dia complete in all respect. ( If Pipe Laid Underground Excavation and refilling cost will be paid extra)
21.12.1 | 32mm dia | Mtr | 437 | 83
21.12.2 | 40 mm dia. | Mtr | 515 | 111
21.12.3 | 50 mm dia. | Mtr | 705 | 139
21.12.4 | 65 mm dia. | Mtr | 909 | 167
21.12.5 | 80 mm dia. | Mtr | 1102 | 194
21.12.6 | 100 mm dia. | Mtr | 1536 | 222
21.13 | SITC of IP 54 OEM Fabricated DOL/Star-Delta Starter panel with switchgear selection as per Type-2 Coordination Chart and made out from 1.6 mm thick powder coated CRCA sheet, enclosure comprising of over load protection relay, short circuit & single phasing protection(for three phase pumps), Illuminated ON / OFF push buttons, ammeter, voltmeter, indicating lamps, 2P/4P MCB etc. suitable for following rating motors complete in all respect.
21.13.1 | For single phase Submersible / Monoblock pump
21.13.1.1 | 0.5 HP to 1.5 HP (DOL starter) | Each | 5643 | 556
21.13.1.2 | 2.0 HP to 3.0 HP (DOL starter) | Each | 6380 | 556
21.13.1.2 | 5.0 HP (DOL starter) | Each | 8601 | 556
21.13.2 | For Three phase Submersible / Mono block pump
21.13.2.1 | Upto 3.0 HP ( DOL starter ) | Each | 8346 | 556
21.13.2.2 | 3.0 HP to 5.0 HP ( DOL starter ) | Each | 11736 | 667
21.13.2.3 | 7.5 HP to 10.0 HP ( DOL starter ) | Each | 15031 | 778
21.13.2.4 | 3.0 HP to 5.0 HP ( Star / Delta starter ) | Each | 15507 | 889
21.13.2.5 | 7.5 HP to 10.0 HP ( Star / Delta starter ) | Each | 16611 | 1111
21.13.2.6 | 12.5 HP to 15.0 HP ( Star / Delta starter ) | Each | 18000 | 1333
21.13.2.7 | 20.0 HP ( Star / Delta starter ) | Each | 22178 | 1667
21.13.2.8 | 25.0 HP ( Star / Delta starter ) | Each | 26257 | 1667
21.13.2.9 | 30.0 HP ( Star / Delta starter ) | Each | 34523 | 2000

## ch 22 Air cooling, HVAC, RO
Chapter E 22
Air Cooling, HVAC, RO and Water Cooler
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
22.1 | Supply , Installation, Testing and Comissioning of factory assembeled double skin central evaporative cooling plant having specifications as per A, B, C, D, E
A. Air washer comprising of 2nos Pre-Filters. First filter shall be 50mm thick Aluminium wiremesh filter & second filter shall be 50 mm thick MERV-8 synthetic media filter with efficiency 90 % down to 10 microns. Both filters to be placed over the common frame.
B. Humidification section comprising of Wet pads 200 mm thick impregnated cellulose paper media ( Celdec pads ) with 2 bend PVC eliminator. The End plates of Pad & Eliminator shall be in SS 304 construction. Also, the inner blank offs of Wet section shall be in SS304 construction.
C. Fan Section comprising of belt driven, DIDW Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 50 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel by means of Spring isolators.
D. TEFC High efficiecny IE-3 class motors as required with pulley, belt , Guard
E. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 25 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. Unit should have MS powder coated legs to give height to unit's base channel from the floor surface. SS-304 ( 18 g ) Sump, UPVC Internal piping, make up, drain & quick fill and drain connection, Butterfly/Gate valves for pumps, make up, drain & quick fill and drain connections of sump, 2 no. Vertical Pumps of suitable capacity to be placed inside the unit's housing (external pumps are not acceptable) ,Y strainers and necessary fittings, Concrete Blocks / M S stand, anti vibration pads etc.as required.
22.1.1 | Upto 7500 cfm | per cfm | 26 | 1.2
22.1.2 | more than 7500 cfm to 15000 cfm | per cfm | 25 | 1.2
22.1.3 | more than 15000 cfm to 25000 cfm | per cfm | 21 | 1
22.1.4 | more than 25000 cfm to 35000 cfm | per cfm | 19 | 1
22.2 | SITC of Wall mounting cubical type Starter panel made out of 1.6 mm thick sheet steel powder coated enclosure designed as per Switchgear OEM type -2 coordination chart and suitable for operation of following cfm range Air Washer's Blower motor, pump comprising of over load protection relay, short circuit & single phasing protection, ON / OFF push buttons, ammeter, voltmeter, indicating lamps, MCB etc. complete in all respect. All as per pre approved by Engineer in charge.
22.2.1 | Upto 7500 cfm | Set | 12137 | 578
22.2.2 | more than 7500 cfm to 15000 cfm | Set | 19276 | 918
22.2.3 | more than 15000 cfm to 25000 cfm | Set | 24036 | 1145
22.2.4 | more than 25000 cfm to 25000 cfm | Set | 28795 | 1371
22.3 | Supply , Installation, Testing and Comissioning of wall mounted remote ON/OFF Push Button station for AHU/Air washers made out from powder quoted CRCA sheet of 16 SWG , illuminated ON/OFF push button including making connections etc as required complete in all respect. All as per pre approved by Engineer in charge. | Set | 5354 | 255
22.4 | P & F of Fire retardent flexible canvass connection made of fibreglass weave having silver grey silicon rubber coating, of height 200 mm with sufficient fold to avoid transmission of vibration with GI frame ,Gasket Nut Bolts for air cooling Plants/AHU/FCU etc as required. | Sq Mtr | 2023 | 96
22.5 | SITC of VFD OEM fabricated VFD cum Bypass starter panel Confirming to IEC60721-3-3, IEC60068-2-60 & IEC60068-2 for variable torque applications, 3C3 avg., 200% torque producing capability at min freq of 0.5 Hz, integrated with 3 to 5% of input reactor or built in DC reactor, Max output frequency 400Hz, built in braking chopper till 30KW, built in RS485 Modbus RTU, Min 7DI, 2DO, 2AI, 1AO, onboard control supply of 24V -150 mA for external operations, RJ45 port, Monitoring parameters – V, I, Torque, Freq, RPM, Watt Hour, DC bus voltage, Analog input V or mA, I/O Status, PID loop monitoring, Torque speed, speed limit, Cooling fan, Protection functions – Ground fault, Over current, Overload, UV/OV, Under/over torque, I/P & O/P phase loss, DBR O/L, inverter over hit alarm, DC bus charge LED indication, heatsink thermistor open detection, stall prevention, fault history of min 4 last faults. Bypass starter shall be provided as per type 2 coordination etc. as required.
22.5.1 | 1.5 KW | Each | 59375 | 2827
22.5.2 | 2.2 KW | Each | 61542 | 2931
22.5.3 | 3.7 KW | Each | 66574 | 3170
22.5.4 | 5.5 KW | Each | 78056 | 3717
22.5.5 | 7.5 KW | Each | 84838 | 4040
22.5.6 | 11.0 KW | Each | 89003 | 4238
22.5.7 | 15.0 KW | Each | 102925 | 4901
22.5.8 | 18.5 KW | Each | 118155 | 5626
22.6 | Supply , Installation, Testing and Comissioning of site fabricated ducting made from GI sheet metal conforming to IS:277 with a zinc coating grade not less than 120 GSM (both side inclusive) & fabricated as per IS:655 and as per approved drawings & designs including the cost of hangers, supports, angle, expansion fasteners , closed cell neoprene gasket T&P etc. as required of following thickness. Test Certificate for Galavanizing with lot no. to be submitted.
22.6.1 | 0.60 mm | Sq Mtr | 920 | 250
22.6.2 | 0.80mm | Sq Mtr | 1093 | 278
22.6.3 | 1.00mm | Sq Mtr | 1283 | 306
22.6.4 | 1.25mm | Sq Mtr | 1514 | 333
22.7 | Supply , Installation, Testing and Comissioning of site fabricated ducting made from aluminium sheet conforming to IS:737, Grade 31000 fabricated as per IS:655 and as per approved drawings & designs including the cost of hangers, supports , angle , expansion fasteners , closed cell neoprene gasket T&P etc. as required of following thickness.
22.7.1 | 0.80 mm | Sq Mtr | 1458 | 278
22.7.2 | 1.00mm | Sq Mtr | 1741 | 306
22.7.3 | 1.20 mm | Sq Mtr | 2024 | 333
22.8 | Supply , Installation, Testing and Comissioning of factory fabricated SMACNA standard ducting made from GI sheet metal conforming to IS:277 with a zinc coating grade of 120GSM (both side inclusive) & fabricated as per IS:655 and as per approved drawings & designs including the cost of hangers, supports, angle, expansion fasteners , closed cell neoprene gasket T&P etc. as required of following thickness.
22.8.1 | 0.60 mm | Sq Mtr | 1224 | 250
22.8.2 | 0.80mm | Sq Mtr | 1468 | 278
22.8.3 | 1.00mm | Sq Mtr | 1767 | 306
22.8.4 | 1.25mm | Sq Mtr | 2112 | 333
22.9 | Supplying, installing, testing and balancing of extruded Aluminium Powder coated supply/return Grilles with fixed bars at front having 0 / 15 / 30 / 45 degrees deflection as required. with Flange size 20 mm with rounded edges including fixing with steel screws etc. complete in all respect. | Sq Mtr | 5548 | 222
22.10 | Supplying, installing, testing and balancing of double louvered of extruded Aluminium Powder coated supply/return air grills of various sizes, Each grill shall be with fixed aerofoil shaped horizontal front bar at 0 deflection and back adjustable vertical louvers, air distribution grid for straightening the air flow through the collar and register including fixing with steel screws etc. complete in all respect.
22.10.1 | Supply air grill with key operated volume control damper | Sq Mtr | 8832 | 333
22.10.2 | Return air grill without volume control damper | Sq Mtr | 7077 | 278
22.11 | Supplying, installing, testing and balancing of extruded Aluminium powder coated Air Diffuser and complete with Flush, 20mm flanges with PVC/neoprene gasket, anti – smudge frame and removable inner core to facilitate the adjustable of air control damper, square/round/ rectangular as required.including fixing with steel screws etc. complete in all respect.
22.11.1 | Supply Air Diffuser with Volume Control damper | Sq Mtr | 10304 | 389
22.11.2 | Return Air Diffuser without Volume Control damper | Sq Mtr | 8266 | 333
22.12 | Supplying, installing and balancing of extruded Aluminium powder coated fresh air inlet louvers with bird screen & volume control damper fixing with steel screws etc. complete in all respect. | Sq Mtr | 7077 | 278
22.13 | Supply , installation, testing & balancing of 20 Gauge G I Damper with brass bushes and 6" pitch multiblade box type galvanised sheet steel construction volume control damper for Ducting and air washers to be provided with suitable links and quadrants for control of volume of air as per specifications complete as required. | Sq Mtr | 5433 | 333
22.14 | Supply and fixing of acoustic lining of ducts with chemically cross link Oxide accetate foam open cell structure Acoustic Insulation with density 30 Kg / Sqm, UV protected and Class O Fire property Water Vapour absorption 0.002 gm / Sqcm, including cost of adhesive etc. complete in all respect.
22.14.1 | 10 mm thick | Sq Mtr | 641 | 111
22.14.2 | 15 mm thick | Sq Mtr | 850 | 133
22.14.3 | 25 mm thick | Sq Mtr | 1246 | 156
22.15 | Supply and fixing duct insulation with 50 mm thick Expanded Polystyrene Thermocol (ESP) sheet of density 24 kg/cu.m after applying two coats of cold setting adhesive (CPRX Compound) and binding sheet with chicken wire mesh and applying cement mortar plaster (1:4) including primer & painting (suitable for outdoor aplication) matching with building colour or as per direction of Engineer incharge as required. | Sq Mtr | 995 | 278
22.16 | Supply and fixing aluminium foil faced 50 mm thick Rock wool insulation of density 36 kg/cu.m after applying two coats of cold setting adhesive (CPRX Compound) sealing all joints with self adhesive tape & finished with 26 G Aluminium cladding. complete in all respect. (For Outdoor applications-air conditioning ducts) | Sq Mtr | 1088 | 278
22.17 | Supply & fixing of external thermal closed-cell Nitrile rubber Insulation material FM/UL approved with high water vapour diffusion resistance and low thermal conductivity should be certified 'Class O' in Fire Propagation as per BS 476 Part 6 in form of sheet on duct including cost of adhesive (CPRX Compound) complete as required.
22.17.1 | 9mm thick with UV paint | Sq Mtr | 591 | 111
22.17.2 | 13mm thick with UV paint | Sq Mtr | 788 | 133
22.17.3 | 13mm thick for Outdoor Application with 26 SWG Aluminium Cladding | Sq Mtr | 1064 | 222
22.17.4 | 19mm thick for Outdoor Application with 26 SWG Aluminium Cladding | Sq Mtr | 1366 | 244
22.18 | Supplying, installing of external thermal closed cell cross linked polyethelene (XLPE) foam insulation made out from non-fibrous, fire retardant (FR), closed cell, tri-dimensional chemically crosslinked polyethylene foam. should be certified 'Class O' in Fire Propagation and 'Class 1' in Surface Spread of Flame as per BS 476 Part 6 & Part 7 respectively in the form of sheet on ducts including cost of adhesive, tape complete as required.
22.18.1 | 9mm thick | Sq Mtr | 566 | 111
22.18.2 | 13mm thick | Sq Mtr | 678 | 111
22.18.3 | 25 mm thick | Sq Mtr | 915 | 111
22.19 | Supply and fixing duct insulation with 50 mm thick Expanded Polystyrene Thermocol (ESP) sheet of density 24 kg/cu.m after applying two coats of cold setting adhesive (CPRX Compound) and binding sheet with chicken wire mesh and applying 26 G aluminium cladding complete as required. | Sq Mtr | 1057 | 278
22.20 | Supply , Installation, Testing and Comissioning of expanded polysterene over deck insulation having thickness of 50 mm and density of 36 Kg / m3 including binding of fibre cloth and applying of two coats of UV paint suitable for exposed atmosphere complete as required. | Sq Mtr | 999 | 139
22.21 | Supplying and fixing of thermal insulation on exposed roof (underdeck) with 25 mm thick Cross Linked Closed Cell Polyethylene FR-XPE insulation of density 33 Kg/m³ with adhesive etc. as required & finally fixed with the help of rawl plug, dash fasteners & adhesive in ceiling of pieces in size of 900x900 mm or 1200x1200 mm. etc. as required. | Sq Mtr | 1070 | 222
22.22 | Supplying, fixing acoustic lining on wall and ceiling of AHU rooms with 50mm thick, density 32 kg/cu.m resin bonded glass fiber insulation friction fixed in 610mm x 610 mm frame work made of 25X50X50X50X25 mm made out of 0.6mm thick GI sheet U shaped channel and covered with reinforced fiber glass tissue and finished with 0.80 mm perforated aluminium sheet etc. complete as required. | Sq Mtr | 887 | 139
22.23 | Supply , Installation, Testing and Comissioning of Window type Air conditioners as per BEE star rating complete with copper power cable upto 3 Mtr, wireless Remote, suitable for working between 230 V +/- 10% with low & high voltage cutoff and 50 Hz ,1 phase AC supply capable of performing, cooling, dehumidification, air circulation R-32/R-410 Green Refrigerant with Scroll / rotary compressor complete with fixing including T&P & labour etc as required complete in all respect as specified of following capacity.
22.23.1 | Cooling capacity 4900 Watt, ISEER not less then 3.1 | Each | 31734 | 1666
22.23.2 | Cooling capacity 7000 Watt, ISEER not less then 3.1 | Each | 38318 | 1666
22.24 | Supply , Installation, Testing and Commissioning of Inverter type Air Cooled Hi Wall split type Air conditioners with latest star rating system as per BEE amended upto date complete with Indoor unit(IDU), Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 3 Mtr (IDU to ODU), copper power cable upto 3.5 Mtr (IDU to ODU), R-32/R-410 Green Refrigerant, wireless Remote control, suitable for working between 230V +/- 10% with low & high voltage cutoff and 50 hz , single phase AC supply capable of performing cooling, dehumidification, air circulation of following capacity with Scroll / rotary compressor. Min 5 year Original Equipment Manufacturer (OEM) warranty of both compressor and Printed Circuit Board (PCB).
22.24.1 | Cooling capacity 3400-3500 Watt, ISEER not less then 3.8 | Each | 33185 | 1666
22.24.2 | Cooling capacity 3400-3500 Watt, ISEER not less then 4.6 | Each | 36935 | 1666
22.24.3 | Cooling capacity 5000-5300 Watt, ISEER not less then 3.8 | Each | 36822 | 1666
22.24.4 | Cooling capacity 5000-5300 Watt, ISEER not less then 4.6 | Each | 46701 | 1666
22.24.5 | Cooling capacity 6200-6350 Watt, ISEER not less then 3.8 | Each | 45992 | 1666
22.24.6 | Cooling capacity 6100- 6300 Watt, ISEER not less then 4.6 | Each | 53311 | 1666
22.24.7 | Cooling capacity 6800-7000 Watt, ISEER not less then 3.8 | Each | 50605 | 2222
22.25 | Supply , Installation, Testing and Commissioning of Inverter type Air cooled Hi Wall split type Air conditioners complete with Indoor unit(IDU), Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 3 Mtr (IDU to ODU), copper power cable upto 3.5 Mtr (IDU to ODU) i/c drain pipe R-32/R-410/ R- 407 Green Refrigerant, wireless Remote control, suitable for working between 180-260V with low & high voltage cutoff and 50 hz ,1 phase AC supply capable of performing cooling, dehumidification, air circulation of following capacity with Scroll / rotary compressor. The system shall be able to deliver 100% of the rated capacity up to 42 Degree Celsius ambient temperature. Min 5 year Original Equipment Manufacturer (OEM) warranty both compressor and Printed Circuit Board (PCB). Must comply : Electrical cable IS 694 or IS 9968 temperature sensing control IS /International Electro technical Commission (IEC) 60730, hermetic compressor IS 10617, heat exchanger IS 11329, capacitor IS 2993 and motor IS 12615. Complete as per specification and IS : 1391 Part II 2023. The system shall be able to operate up to 50 degree C (out door ambient temperature)
22.25.1 | Cooling capacity 3400-3500 Watt, ISEER not less then 3.8 | Each | 35210 | 1666
22.25.2 | Cooling capacity 3400-3500 Watt, ISEER not less then 4.6 | Each | 41103 | 1666
22.25.3 | Cooling capacity 5000-5300 Watt, ISEER not less then 3.8 | Each | 42236 | 1666
22.25.4 | Cooling capacity 5000-5300 Watt, ISEER not less then 4.6 | Each | 49828 | 1666
22.25.5 | Cooling capacity 6200-6350 Watt, ISEER not less then 3.8 | Each | 51075 | 1666
22.25.6 | Cooling capacity 6100- 6300 Watt, ISEER not less then 4.6 | Each | 55834 | 1666
22.25.7 | Cooling capacity 6800-7000 Watt, ISEER not less then 3.8 | Each | 54917 | 2222
22.26 | Supply , Installation, Testing and Commissioning of Air Cooled Floor standing Tower type split Air conditioners complete with Indoor unit(IDU), Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 3 Mtr (IDU to ODU), copper power cable upto 3.5 Mtr (IDU to ODU), R-32/R-410 Green Refrigerant, wireless Remote control, suitable for working between 415 V +/- 10% ,3 phase 50 Hz AC Supply with low & high voltage cutoff and capable of performing cooling, dehumidification, air circulation of following capacity with Scroll / rotary compressor.
22.26.1 | Cooling capacity 6800 Watt, ISEER not less then 3.0 | Each | 83292 | 3966
22.26.2 | Cooling capacity 10400 - 10500 Watt, ISEER not less then 3.0 | Each | 115418 | 5496
22.26.3 | Cooling capacity 14000 Watt, ISEER not less then 3.0 | Each | 132672 | 6318
22.27 | SITC of air cooled ducted split type air conditioning machine with each having a capacity and details as mentioned below suitable for operation on factory charged R-32/R-410A Green refrigerant comprising of Scroll /rotary type compressor hermatically sealed complete with automatic capacity, safety switches, lubrication system, Suitable capacity squirrel cage induction motor with class 'B' insulation suitable for operation on single / three phase supply, 50 Hz, A.C. supply for Blower motor, Necessary drive arrangement for blower motor, Matching Air cooled condenser with necessary fittings for refrigerant piping connections, necessary structural support for mounting condensers, Microprocessor based control panel complete with accessories, machine isolation / disconnect switch, valves and accessories to interconnect compressor and condenser including pressure testing, vacuum. Necessary starters suitable for Indoor & outdoor unit with O/L , U/V, phase reversal protection, single phase preventors etc complete as required.
22.27.1 | Non Invertor Type (Fix Speed)
22.27.1.1 | Cooling Capacity 10400-10600 Watt | Each | 78626 | 3744
22.27.1.2 | Cooling Capacity 13900-14200 Watt | Each | 86005 | 4096
22.27.1.3 | Cooling Capacity 17500-18000 Watt | Each | 119052 | 5669
22.27.1.4 | Cooling Capacity 29500-30000 Watt (single Ckt) | Each | 178892 | 8519
22.27.1.5 | Cooling Capacity 37000-37500 Watt (Double Ckt) | Each | 216665 | 10317
22.27.1.6 | Cooling Capacity 53000-53500 Watt (Double Ckt) | Each | 324282 | 15442
22.27.2 | Invertor Type
22.27.2.1 | Cooling Capacity 18500-19000 Watt | Each | 155982 | 7428
22.27.2.2 | Cooling Capacity 28000-28500 Watt | Each | 211174 | 7428
22.27.2.3 | Cooling Capacity 35000-36000 Watt | Each | 272620 | 12982
22.27.2.4 | Cooling Capacity 53000-53500 Watt | Each | 372427 | 17735
22.28 | Supply , Installation, Testing and Commissioning of Inverter type Air Cooled Cassette type Air conditioners complete with Indoor unit(IDU), Out door unit (ODU), R-32/R410A Green Refrigerant, wireless Remote, inbuilt drain pump, suitable for 400/230V, +/- 10% 50 Hz ,1 /3 phase AC supply, capable of performing cooling, dehumidification, Air circulation, filteration & ventilation of following capacity with Scroll /rotary/twin rotary compressor etc. complete as required.
22.28.1 | Cooling Capacity 5000-5100 Watt ISEER not less then 3.5 | Each | 75519 | 3596
22.28.2 | Cooling Capacity 6900-7000 Watt ISEER not less then 3.5 | Each | 88622 | 4220
22.28.3 | Cooling Capacity 10500-11000 Watt ISEER not less then 3.5 | Each | 115836 | 5516
22.28.4 | Cooling Capacity 14000-14700 Watt ISEER not less then 3.5 | Each | 133639 | 6364
22.29 | Supply, Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling & heating, having 100% hermetically sealed inverter type twin rotary/Scroll Compressor(s) with and minimum two compressors , above 14 HP modules, microprocessor based Controller, Side / top discharge type condensing unit(s), with R-410 A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The EER/COP (W/W) at 100% load with AHRI conditions shall not be less than 3.8 etc. complete as required.
22.29.1 | 6 HP to 8 HP | Per HP | 24512 | 714
22.29.2 | 10 HP to 12 HP | Per HP | 22761 | 663
22.29.3 | 14 HP to 26 HP | Per HP | 21010 | 612
22.30 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down valve in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor).
22.30.1 | 0.8 TR (Cooling Capacity 2800 Watt) | Each | 40158 | 1912
22.30.2 | 1.0 TR (Cooling Capacity 3500 Watt) | Each | 40753 | 1941
22.30.3 | 1.3 TR (Cooling Capacity 4500 Watt) | Each | 41348 | 1969
22.30.4 | 1.6 TR (Cooling Capacity 5600 Watt) | Each | 42538 | 2026
22.30.5 | 2.0 TR (Cooling Capacity 7100 Watt) | Each | 43371 | 2065
22.30.6 | 2.4 TR (Cooling Capacity 8700 Watt) | Each | 44502 | 2119
22.30.7 | 3.0 TR (Cooling Capacity 11200 Watt) | Each | 45810 | 2181
22.30.8 | 4.0 TR (Cooling Capacity 14000 Watt) | Each | 49380 | 2351
22.30.9 | 4.5 TR (Cooling Capacity 15700 Watt) | Each | 52117 | 2482
22.31 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow compact VRV/VRF Cassette ( 2' x 2' ) Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down valve in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor)
22.31.1 | 0.6 TR (Cooling Capacity 2200 Watt) | Each | 40158 | 1912
22.31.2 | 0.8 TR(Cooling Capacity 2800 Watt) | Each | 40753 | 1941
22.31.3 | 1.0 TR (Cooling Capacity 3500 Watt) | Each | 41348 | 1969
22.31.4 | 1.2 / 1.3 TR (Cooling Capacity 4500 Watt) | Each | 42538 | 2026
22.31.5 | 1.5 / 1.6 TR (Cooling Capacity 5600 Watt) | Each | 44918 | 2139
22.32 | SITC of following minimum capacity one way wall/corner VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump,grill,necessarysupports,vibration Isolation, etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply complete, as required. The Indoor units must shut down upon receiving a singal from the BMS System/Fire Signals. The system shall be capable to adjust air flow as per room requirement automatically. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor)
22.32.1 | 1.0 TR (Cooling Capacity 3500 Watt) | Each | 53485 | 2547
22.32.2 | 1.3 TR (Cooling Capacity 4500 Watt) | Each | 56519 | 2691
22.32.3 | 1.6 TR (Cooling Capacity 5600 Watt) | Each | 57828 | 2754
22.32.4 | 2.0 TR (Cooling Capacity 7000 Watt) | Each | 58840 | 2802
22.33 | Supply, Installation, Testing and Commissioning of following minimum capacity two way VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports,vibration Isolation,etc.,suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The Indoor units must shut down upon receiving a singal from the BMS System/Fire Signals. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor)
22.33.1 | 1.6 TR (Cooling Capacity 5600 Watt) | Each | 77045 | 3669
22.33.2 | 2.0 TR (Cooling Capacity 7000 Watt) | Each | 80614 | 3839
22.33.3 | 2.6 TR (Cooling Capacity 9000 Watt) | Each | 94001 | 4476
22.33.4 | 4.0 TR (Cooling Capacity 14000 Watt) | Each | 108279 | 5156
22.34 | Add Extra for OEM make Wireless remote for Indoor unit including receiver as required. | Each | 3808 | 181
22.35 | Supply, installation, testing and commissioning of following minimum capacity VRV/VRF High wall type Indoor unit equipped with and comfort washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cord less remote control, drain pan, necessary accessories etc., suitable for operation on 230 V ± 10%, 50 Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down valve in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor)
22.35.1 | 0.6 TR (Cooling capacity 2200 watt) | Each | 23322 | 1111
22.35.2 | 0.8 TR (Cooling capacity 2800 watt) | Each | 24274 | 1156
22.35.3 | 1.0 TR (Cooling capacity 3500 watt) | Each | 24940 | 1188
22.35.4 | 1.3 TR (Cooling capacity 4500 watt) | Each | 26177 | 1246
22.35.5 | 1.6 TR (Cooling capacity 5600 watt) | Each | 27129 | 1292
22.35.6 | 2.0 TR (Cooling capacity 7000 watt) | Each | 28557 | 1360
22.35.7 | 2.5 TR (Cooling capacity 8700 watt) | Each | 38076 | 1813
22.35.8 | 2.9 TR (Cooling capacity 10000 watt) | Each | 42836 | 2040
22.36 | Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, drain pump, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down valve in case of fire on receiveing signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor)
22.36.1 | Mid Static Ductable units ( 30 to 77 pascal external static pressure)
22.36.1.1 | 1.6 TR (Cooling capacity 5600 Watt) 650 cfm | Each | 28617 | 1363
22.36.1.2 | 2.0 TR (Cooling capacity 7000 Watt) 800 cfm | Each | 29688 | 1414
22.36.1.3 | 2.6 TR (Cooling capacity 9000 Watt) 1000 cfm | Each | 30639 | 1459
22.36.1.4 | 3.0 TR (Cooling capacity 11000 Watt) 1200 cfm | Each | 31234 | 1487
22.36.2 | High Static Ductable units ( 78 pascal or above external static pressure)
22.36.2.1 | 4.0 TR (Cooling capacity 14000 Watt) 1350 cfm | Each | 69608 | 3315
22.36.2.2 | 4.5 TR (Cooling capacity 15700 Watt) 1600 cfm | Each | 76152 | 3626
22.36.2.3 | 5.5 TR (Cooling capacity 19000 Watt) 2000 cfm | Each | 81626 | 3887
22.36.2.4 | 6.6 TR (Cooling capacity 22000 Watt) 2400 cfm | Each | 138502 | 6595
22.36.2.5 | 8.0 TR (Cooling capacity 28000 Watt) 2800 cfm | Each | 158016 | 7525
22.36.2.6 | 11.0 TR (Cooling capacity 38000 Watt) 4000 cfm | Each | 158016 | 7525
22.37 | SITC of VRF OEM manufactured treated fresh air unit (TFA) equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section with DX coil, outer cabinet, insulated drain pan, pipe connections etc. of following Nominal capacities with tolerance +/- 5% (Make will be same as of Outdoor)
22.37.1 | 4.0 TR/700 CFM | job | 58899 | 2805
22.37.2 | 6.5 TR/1000 CFM | job | 88646 | 4221
22.37.3 | 8.0 TR/1350 CFM | job | 102925 | 4901
22.37.4 | 10 TR/1750 CFM | job | 157064 | 7479
22.38 | Supply, installation, testing & commissioning of Group controller for monitoring the status and working condition of all indoor and outdoor units, The controller shall act as an advanced air conditioning management system to given complete control of VRV/VRF air conditioning equipment with Starting/stopping of air-conditioning as a zone or group of individual units. Temperature setting for each Indoor units of zone, Switching between temperature control modes, switching of the fan speed and direction of airflow, enabling/disabling of individual remote controller operation, Alarm code display in case of any problem. It shall be able to control up to 64 number of Indoor units. | Each | 41646 | 1983
22.38.1 | Add Extra for extenders/adaptors compatible with central controller to enable the controller to work with 128 IDU's | Each | 14874 | 708
22.38.2 | Add Extra for extenders/adaptors compatible with central controller to enable the controller to work with 256 IDU's | Each | 26772 | 1275
22.38.3 | Add Extra for extenders/adaptors compatible with central controller to enable the controller to work with 512 IDU's | Each | 62469 | 2975
22.39 | Supply, installation, Testing & commissioning of VRV/VRF compatible OEM make AHU KIT' including expansion valve and controller for connecting AHU with VRF complete as required.. | Each | 46405 | 2210
22.40. | Supplying and installation of high-pressure grade required size OEM make copper connection Y or T Joints / refnet for liquid and suction line , complete erected on wall/ceiling with supports/raceways, Nitrile rubber insulation, painting etc. with brazing and testing for leakages confirming the normal operation of the VRV / VRF air conditioning system complete as required. | Each | 5830 | 278
22.41 | Gas charging of VRF/VRV system with R410A refrigerant gas. Before gas charging system shall be flushed with high purity Nitrogen Gas to remove carbon content, dirt particles to make sure that there is no chance of mixing any impurity with Refrigerant Gas. Thereafter System shall be tested with Nitrogen Gas at 1.5 Times of working pressure of R410 Refrigerant Gas to ensure leakproof system. Whole system shall be Vacuumed up to 500-micron level which ensures the zero-moisture content level in piping to ensure better cooling efficiency and long life of the system. | per Kg | 1428 | 68
22.42 | Supplying and drawing flexible / stranded bare copper conductor, PVC / XLPE insulated, overall aluminium mylar tape shielded ATC drain wire and outer PVC sheathed industrial Instrumentation (shielded)cables voltage grade 300/500 V as per BS /EN 50288-7 in existing surface or recessed PVC/ MS conduit/casing capping / Cable tray / Open Duct making connections, testing etc. as required. OEM must ensure that the cable is tested for complaince, either through their in house laboratory accrediated by NABL or by any Govt. laboratory accrediated by NABL and the laboratory's scope of accrediation should cover the requirements and testing procedure as per IS:10810.
22.42.1 | Un Armoured
22.42.1.1 | 2 core x 1.0 Sq.mm | mtr | 55 | 3
22.42.1.2 | 2 core x 1.5 Sq.mm | mtr | 71 | 3
22.42.1.3 | 2 core x 2.5 Sq.mm | mtr | 105 | 5
22.42.1.4 | 4 core x 2.5 Sq.mm | mtr | 187 | 9
22.42.2 | Armoured
22.42.2.1 | 2 core x 1.0 Sq.mm | mtr | 101 | 5
22.42.2.2 | 2 core x 1.5 Sq.mm | mtr | 121 | 6
22.42.2.3 | 2 core x 2.5 Sq.mm | mtr | 162 | 8
22.42.2.4 | 4 core x 2.5 Sq.mm | mtr | 266 | 13
22.43 | Supply, installation, testing and commissioning of interconnecting copper refrigerant piping of DHE Grade C12200- ASTM B68, B75, chemical composition of copper %- 99.0 Min and Phosphorus %- 0.015 to 0.040 . For Annealed copper tube :- Tensile strength = 210 Mpa wih elongation % = 40 Min . Ink Mark Brand Printing on Hard Tubes should be present. duly insulated with tubular elastomeric nitrile rubber FM/UL approved with high water vapor diffusion resistance and low thermal conductivity should be certified 'Class O' in Fire Propagation as per BS 476 Part 6 with 7 mil Glass Cloth and 3 coats of anti UV paint (on area which is exposed to weather) including chase cutting andfilling with mortar, Slotted channel supports mounted on 10 mm threaded rod at suitable spacing the exposed piping shall be wrapped with glass woven cloth and lag coating for vapour barrier and weather protection. Joints shall be covered with nitrile rubber tape of 3 mm thick complete as required of following sizes.
22.43.1 | 41.1 mm O.D., wall thinkness ≥ 1.4mm (insulation – 19 mm thick) | mtr | 3742 | 178
22.43.2 | 38 mm O.D., wall thinkness ≥ 1.4mm (insulation – 19 mm thick) | mtr | 3492 | 166
22.43.3 | 34.9 mm O.D., wall thinkness ≥ 1.4mm (insulation – 19 mm thick) | mtr | 2933 | 140
22.43.4 | 28.6 mm O.D., wall thinkness ≥ 1.2mm (insulation – 19 mm thick) | mtr | 2255 | 107
22.43.5 | 25 mm O.D., wall thinkness ≥ 1.2mm (insulation – 19 mm thick) | mtr | 1874 | 89
22.43.6 | 22.2 mm O.D., wall thinkness ≥ 1.0mm (insulation – 19 mm thick) | mtr | 1612 | 77
22.43.7 | 19.1 mm O.D., wall thinkness ≥ 1.0mm (insulation – 13 mm thick) | mtr | 1166 | 55
22.43.8 | 15.9 mm O.D., wall thinkness ≥ 0.8mm (insulation – 13 mm thick) | mtr | 970 | 46
22.43.9 | 12.7 mm O.D., wall thinkness ≥ 0.8mm (insulation – 13 mm thick) | mtr | 714 | 34
22.43.10 | 9.5 mm O.D., wall thinkness ≥ 0.8mm (insulation – 13 mm thick) | mtr | 512 | 24
22.43.11 | 6.4 mm O.D., wall thinkness ≥ 0.8mm (insulation – 13 mm thick) | mtr | 363 | 17
22.44 | Providing & Fixing of IS : 4985 - 2000 Class -4 (10 Kgf / Sqcm) UPVC drain water piping with fittings (IS:7834 & 10Kgf/sqcm) like elbow, socket, Tee, solvent cement jointing, support with MS hanger on ceiling or recessed in wall with chasing & plastering with 6 mm thick closed cell elastomeric nitrile rubber insulation including leakage testing etc. as required of following Nominal sizes.
22.44.1 | 20 mm | mtr | 131 | 6
22.44.2 | 25 mm | mtr | 155 | 7
22.44.3 | 32 mm | mtr | 208 | 10
22.44.4 | 40 mm | mtr | 244 | 12
22.44.5 | 50 mm | mtr | 303 | 14
22.44.6 | 63 mm | mtr | 381 | 18
22.45 | Supply, Fixing and testing of following capacity IS:8448 marked wall mounted stabilizer having output voltage variation from 200 V to 250 V(+/-5%) with input voltage variation from 170 V to 260 V, time delay facility from 2 to 4 minute and high cutoff at 270 V with providing of 16 Amp /20 Amp Industrial plug top making connection etc complete in all respect.
22.45.1 | 3 kVA | Each | 2499 | 119
22.45.2 | 4 KVA | Each | 2856 | 136
22.45.3 | 5 kVA | Each | 3570 | 170
22.46 | Making hole in stone masonary/ RCC wall/ RCC slab with core cutter for accomodating refrigerant pipe/ drain pipe/ MS pipe/ cables etc of following dia
22.46.1 | 50 mm dia per running inch length | per inch | 67 | 67
22.46.2 | 100 mm dia per running inch length | per inch | 133 | 133
22.46.3 | 150 mm dia per running inch length | per inch | 200 | 200
22.46.4 | 200 mm dia per running inch length | per inch | 278 | 278
22.47 | Providing and making wall openings in existing stone / Brick masonry partition wall complete with all requited T & P, Scaffolding and providing lintel of required size and strength, repairing, plastering and cleaning the site debris as required. | Cuft | 613 | 613
22.48 | Supply & fixing MS powder coated stand suitable for 1.0/1.5/ 2.0 Tr outdoor type of Split AC. All as per pre approved by Engineer in charge. | Each | 542 | 111
22.49 | Supply & fixing MS powder coated stand suitable for 2.5/3.0/4.0 Tr outdoor type of Split/Ductable/Tower AC. All as per pre approved by Engineer in charge. | Each | 1130 | 167
22.50. | P & F of trap door for AHU / FCU's in existing false ceiling duly made from 12 mm thick laminated board, hinged with wooden frame of cheed wood size 50mm x 80mm, Frame suspended with MS strip 25 x 3 mm with anchor fastner min 8 supports from ceiling, Hinges, Locking arrangement etc as required. | Sqm | 4577 | 611
22.51 | SITC of Condensate water Drain pump suitable to Install with Existing Split type AC Indoor unit , single phase, 230V, including all acessories of pump like discharge tube, filter, reservoir etc. as required. | job | 5354 | 255
22.52 | SITC of Interconnecting refrigerant copper pipe for split/Ductable/ Casseette AC of DHE Grade C12200- ASTM B68, B75, chemical composition of copper %- 99.0 Min and Phosphorus %- 0.015 to 0.040 . For Annealed copper tube :- Tensile strength = 210 Mpa wih elongation % = 40 Min . Ink Mark Brand Printing on Hard Tubes should be present. Piping between each set of indoor & outdoor units of different sizes as per OEM requirement & specifications including class 'O' Nitrile rubber sleeves (size as per item no. 22.43),7 mil Glass Cloth with 3 coats of anti UV paint (on area which is exposed to weather) chase cutting, supports, making good the same with sand cement plaster etc. as required. | Per Kg | 2203 | 367
22.53 | SITC of BMS compatible, fixed speed multi compressors modular Air Cooled scroll type chillers of following Nominal cooling capacity complete with fixed speed multi compressors (Min. 2/3 per chiller) fully hermetic scroll compressors, 2/3 fan motor, starter, air-cooled condenser with fins, evaporator of Shell & Tube / PHE type, vibration isolators, inbuilt accumulator, environment friendly refrigerant R-410A, first charge of refrigerant and oil, wiring, all accessories as per specifications, automatic and safety controls, microprocessor control panel, all mounted on steel frame, all accessories and any other item required to make the system complete. Modular Design to allow connection of multiple machines to make them behave as one unit. And the overall set to continue working in case of break down of one module. modular unit should have master and slave arrangement to run in single circuit of required unit as one. including wired remote controller for each unit and master controller to operate all chiller in one circuit. Chilled water Leaving Temp.(6.67 deg. C) Chilled water Entering Temp.(12.2 deg. C) Evaporator fouling factor = 0.018 m2. ⁰C/kW Condenser air entering temp. : As per Site Dry Bulb Temperature Suitable for climatic Zone and Altitude as per location/site.
22.53.1 | 6 TR to 12 TR with ISEER > / = 3.6 | per TR | 29884 | 1666
22.53.2 | More than 12 TR to 24 TR with ISEER > / = 3.6 | per TR | 27904 | 1500
22.53.3 | more than 24 TR to 36 TR with ISEER > / = 3.6 | per TR | 25866 | 1389
22.54 | SITC of AHRI (Air-Conditioning, Heating, and Refrigeration Institute) Certified Air-Cooled Screw Chiller package complete with VFD (Variable Frequency Drive), hermetic/semi hermetic, screw type compressor each with step less capacity control of 25 % to 100 % of the rated capacity, with microprocessor based control panel compatible for BMS operation, motor, starter panel (VFD), machine mounted, air- cooled condensers with Copper tube and Aluminium fins, factory fitted chiller insulation, water flow switch, vibration spring Isolators, victaulic couplings, integral refrigerant piping and wiring with single/ two circuits, automatic and safety controls mounted in central console panel and all mounted on a steel frame (complete as per specifications) on existing RCC foundation / M S Structure, anti vibration pad, power control cable and connection inter connection etc. as per design approved by engineer-in-charge. Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply. Refrigerant gas used shall be R-134A. The chiller shall be Building Management System (BMS) compatible The system shall be in confirmation to IS : 16590. Chilled water Leaving Temp.(6.67 deg. C) Chilled water Entering Temp.(12.2 deg. C) Evaporator fouling factor = 0.018 m2. ⁰C/kW Condenser air entering temp. : As per Site Dry Bulb Temperature Suitable for climatic Zone and Altitude as per location/site.
22.54.1 | Upto 74 TR with ISEER > / = 3.6 | per TR | 28419 | 1222
22.54.2 | 75 TR - 140 TR with ISEER > / = 3.9 | per TR | 27062 | 1111
22.55 | SITC of floor-mounted AHRI (Air-Conditioning, Heating, and Refrigeration Institute) Certified water cooled screw-type chiller machine complete with VFD (Variable Frequency Drive), single/multi semi-hermatic twin screw type compressor, water-cooled Shell & Tube type condenser, Shell & Tube horizontal flooded type evaporator with carbon steel shell and seamless copper tubes with 19 mm nitrile rubber insulation on existing RCC foundation / M S Structure, anti vibration pad, power control cable and connection inter connection etc. as per design approved by engineer-in-charge, interconnected copper refrigerant piping and wiring, vibration Isolators, gauge panel, automatic safety controls, chiller Mounted Star-Delta starter with suitable MCCB, complete with accessories as required flow switch at evaporator and condenser and ozone friendly Chlorofluorocarbons (CFC)-free refrigerant gas R-134A. The refrigerant flow control shall use an electronic expansion valve. The chiller shall be designed for a Water Side working pressure of 150 PSI and hydraulically tested at 1.3 times of design pressure . A number of properly spaced baﬄes shall be provided for maintaining optimum water velocity and heat transfer and the tubes shall be adequately supported. The chiller shall be Building Management System (BMS) compatible The system shall be in confirmation to IS : 16590. Chilled water Leaving Temp.(6.67 deg. C) Chilled water Entering Temp. (12.2 deg. C) Evaporator fouling factor = 0.018 m2. ⁰C/kW , Condensor Fouling Factor 0.088 m2. ⁰C/kW Condenser water Entering Temp. (32.2 deg. C) Condenser water Leaving Temp. (36.4 deg. C) Suitable for Climatic Zone and Altitude as per location/site.
22.55.1 | Upto 70 TR with ISEER > / = 5.60 | per TR | 23830 | 1222
22.55.2 | 71 TR - 110 TR with ISEER > / = 6.20 | per TR | 21396 | 1111
22.55.3 | 111 TR - 150 TR with ISEER > / = 6.20 | per TR | 19811 | 1000
22.55.4 | 151 TR - 210 TR with ISEER > / = 6.70 | per TR | 18794 | 889
22.55.5 | 211 TR - 260 TR with ISEER > / = 6.70 | per TR | 17776 | 778
22.55.6 | 261 TR - 300 TR with ISEER > / = 6.70 | per TR | 16869 | 778
22.56 | Supply of Induced Draft counterflow cooling Towers(CTI approved). The Cooling Tower shall be of Fiber Reinforced Plastic (FRP) Construction. The casing, basin/sump, fan deck and fan cylinder shall be of FRP, with direct driven fans, Galvanised hardware complete with sump and drain connection with suitable valve, PVC Honey comb fill, louvers, drift eliminator complete with spray nozzle having self rotating sprinklers, steel ladder, Isolating switch and other accessories to make it fully operational & positioning of cooling tower on existing MS / RCC structure. Propeller Type Fan, weather proof IP 55 and Direct driven.The fan motor shall be premium eﬃciency IE3 class , as per IS 12615 The Cooling tower shall be capable to communicate effectively with Building Management System (BMS). Range of CT: 6 deg C. Designed Duty Conditions :- EWT, LWT , D/WBT Complete as directed by Engineer-in-charge. (Note - Cooling tower size depends on the ambient temperature conditions , contractor must check the required design temperature).
22.56.1 | 300 GPM | Each | 227586 | 20320
22.56.2 | 450 GPM | Each | 305107 | 27242
22.56.3 | 600 GPM | Each | 418962 | 37407
22.56.4 | 750 GPM | Each | 563677 | 50328
22.56.5 | 900 GPM | Each | 656876 | 58650
22.56.6 | 1050 GPM | Each | 729172 | 65105
22.56.7 | 1200 GPM | Each | 832699 | 74348
22.56.8 | 1350 GPM | Each | 884463 | 78970
22.56.9 | 1500 GPM | Each | 972312 | 86814
22.57 | SITC of following discharge and head, End suction chilled water/ Condensor water recirculation pumps complete with motor , base frame, vibration isolators, mechanical seal, Bronze/S.S. Impeller. The pump motor shall be suitable for 415 ± 10%, 50 cycles, 3 phase power supply, squirrel cage induction 1450 RPM TEFC, IE3 motor, class 'F' insulation, with vibration isolators on existing MS / RCC foundation.
22.57.1 | Primary chilled water pump
22.57.1.1 | Flow rate : 200 USGPM, Head : 15 Mtr. | Each | 122939 | 10977
22.57.1.2 | Flow rate : 300 USGPM, Head : 15 Mtr. | Each | 151664 | 13541
22.57.1.3 | Flow rate : 500 USGPM, Head : 15 Mtr. | Each | 171673 | 15328
22.57.1.4 | Flow rate : 700 USGPM, Head : 15 Mtr. | Each | 234411 | 20930
22.57.1.5 | Flow rate : 900 USGPM, Head : 15 Mtr. | Each | 243041 | 21700
22.57.2 | Secondary chilled water pump with VFD (Stand alone or integrated)
22.57.2.1 | Flow rate : 200 USGPM, Head : 25 Mtr. | Each | 246587 | 22017
22.57.2.2 | Flow rate : 300 USGPM, Head : 25 Mtr. | Each | 265453 | 23701
22.57.2.3 | Flow rate : 500 USGPM, Head : 25 Mtr. | Each | 375436 | 33521
22.57.2.4 | Flow rate : 700 USGPM, Head : 25 Mtr. | Each | 478752 | 42746
22.57.2.5 | Flow rate : 900 USGPM, Head : 25 Mtr. | Each | 486637 | 43450
22.57.2.6 | Flow rate : 200 USGPM, Head : 40 Mtr. | Each | 312076 | 27864
22.57.2.7 | Flow rate : 300 USGPM, Head : 40 Mtr. | Each | 367930 | 32851
22.57.2.8 | Flow rate : 500 USGPM, Head : 40 Mtr. | Each | 408535 | 36476
22.57.2.9 | Flow rate : 700 USGPM, Head : 40 Mtr. | Each | 620605 | 55411
22.57.2.10 | Flow rate : 900 USGPM, Head : 40 Mtr. | Each | 705362 | 62979
22.57.3 | Condensor water pump
22.57.3.1 | Flow rate : 300 USGPM, Head : 20 Mtr. | Each | 176665 | 15774
22.57.3.2 | Flow rate : 500 USGPM, Head : 20 Mtr. | Each | 221290 | 19758
22.57.3.3 | Flow rate : 700 USGPM, Head : 20 Mtr. | Each | 258290 | 23062
22.57.3.4 | Flow rate : 900 USGPM, Head : 20 Mtr. | Each | 266683 | 23811
22.57.3.5 | Flow rate : 1100 USGPM, Head : 20 Mtr. | Each | 350730 | 31315
22.57.3.6 | Flow rate : 300 USGPM, Head : 45 Mtr. | Each | 215143 | 19209
22.57.3.7 | Flow rate : 500 USGPM, Head : 45 Mtr. | Each | 287842 | 25700
22.57.3.8 | Flow rate : 700 USGPM, Head : 45 Mtr. | Each | 365270 | 32613
22.57.3.9 | Flow rate : 900 USGPM, Head : 45 Mtr. | Each | 416219 | 37162
22.57.2.10 | Flow rate : 1100 USGPM, Head : 45 Mtr. | Each | 462203 | 41268
22.58 | SITC of factory assembeled Ceiling suspended double skin Air Handling Unit having specifications as per A, B, C, D & E
A. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
B. Coil Section : Coil section with 6 rows (3+3)deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
C. Fan Section : Fan Section comprising of belt driven, DIDW forward / Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 40 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel.
D. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
E. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. ,The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts. noise level shall not exceed 70 dB, necessary vibration Isolation arrangement like spring hanger etc. as required.
22.58.1 | 500 cfm to 2000 cfm | per cfm | 52 | 5
22.58.2 | more than 2000 cfm to 4000 cfm | per cfm | 49 | 4
22.58.3 | more than 4000 cfm to 6000 cfm | per cfm | 47 | 4
22.58.4 | 500 cfm to 2000 cfm with 8 Row deep coil for TFA | per cfm | 57 | 5
22.58.5 | more than 2000 cfm to 4000 cfm with 8 Row deep coil for TFA | per cfm | 54 | 5
22.58.6 | more than 4000 cfm to 6000 cfm with 8 Row deep coil for TFA | per cfm | 52 | 5
22.59 | SITC of factory assembeled Ceiling suspended double skin Air Handling Unit having specifications as per A, B, C, D, E & F
A. Mixing Box : Mixing box with manually operated fresh air and return air dampers in aluminium construction
B. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
C. Coil Section : Coil section with 6 rows (3+3) deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
D. Fan Section : Fan Section comprising of belt driven, DIDW forward / Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 50 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel.
E. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
F. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. ,The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts. noise level shall not exceed 70 dB, necessary vibration Isolation arrangement like spring hanger etc. as required.
22.59.1 | 500 cfm to 2000 cfm | per cfm | 57 | 5
22.59.2 | more than 2000 cfm to 4000 cfm | per cfm | 54 | 5
22.59.3 | more than 4000 cfm to 6000 cfm | per cfm | 52 | 5
22.60 | SITC of factory assembeled Ceiling suspended double skin Air Handling Unit having specifications as per A, B, C, D, E, F & G
A. Mixing Box : Mixing box with manually operated fresh air and return air damoers in aluminium construction
B. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
C. Fine Filter section : Fine filter section with 305 mm thick fine filetrs complete with fine filters. Velocity across fine filters shall not exceed 500FPM. Filters shall have efficiency not less than 99% down to 3 Microns (EU-7/MERV-13). Filter material shall be non combustible type.
D. Coil Section : Coil section with 6 row (3+3) deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
E. Fan Section : Fan Section comprising of belt driven, DIDW Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 70 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel.
F. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
G.The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. ,The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts. noise level shall not exceed 70 dB, necessary vibration Isolation arrangement like spring hanger etc. as required.
22.60.1 | 500 cfm to 2000 cfm | per cfm | 67 | 6
22.60.2 | more than 2000 cfm to 4000 cfm | per cfm | 65 | 6
22.60.3 | more than 4000 cfm to 6000 cfm | per cfm | 62 | 505
22.61 | SITC of factory assembeled Floor mounted double skin Air Handling Unit having specifications as per A, B, C, D & E
A. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
B. Coil Section : Coil section with 6 rows (3+3) deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
C. Fan Section : Fan Section comprising of belt driven, DIDW Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 40 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel by means of Spring isolators.
D. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
E. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. mounted on GSS base channel, The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts.necessary vibration Isolation arrangement, noise level shall not exceed 70 dB
22.61.1 | 3000 cfm to 8000 cfm | per cfm | 49 | 4
22.61.2 | more than 8000 cfm to 13000 cfm | per cfm | 47 | 4
22.61.3 | more than 13000 cfm to 18000 cfm | per cfm | 44 | 4
22.61.4 | more than 18000 cfm to 23000 cfm | per cfm | 42 | 4
22.61.5 | more than 23000 cfm to 30000 cfm | per cfm | 40 | 4
22.61.6 | more than 30000 cfm to 40000 cfm | per cfm | 38 | 3
22.61.7 | more than 40000 cfm to 50000 cfm | per cfm | 36 | 3
22.62 | SITC of factory assembeled Floor mounted double skin Air Handling Unit having specifications as per A, B, C, D, E & F
A. Mixing Box : Mixing box with manually operated fresh air and return air damoers in aluminium construction
B. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
C. Coil Section : Coil section with 6 rows (3+3) deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
D. Fan Section : Fan Section comprising of belt driven, DIDW Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 50 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel by means of Spring isolators.
E. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
F.The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. mounted on GSS base channel, The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts.necessary vibration Isolation arrangement, noise level shall not exceed 70 dB
22.62.1 | 3000 cfm to 8000 cfm | per cfm | 57 | 5
22.62.2 | more than 8000 cfm to 13000 cfm | per cfm | 55 | 5
22.62.3 | more than 13000 cfm to 18000 cfm | per cfm | 53 | 5
22.62.4 | more than 18000 cfm to 23000 cfm | per cfm | 51 | 4.5
22.62.5 | more than 23000 cfm to 30000 cfm | per cfm | 49 | 4
22.62.6 | more than 30000 cfm to 40000 cfm | per cfm | 46 | 4
22.62.7 | more than 40000 cfm to 50000 cfm | per cfm | 44 | 4
22.63 | SITC of factory assembeled Floor mounted double skin Air Handling Unit having specifications as per A, B, C, D, E, F & G
A. Mixing Box : Mixing box with manually operated fresh air and return air damoers in aluminium construction
B. Pre filter section : Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 500 FPM. Filters shall have efficiency not less than 90% down to 10 Microns (EU-4/MERV-8). Filter material shall be non combustible type.
C. Fine Filter section : Fine filter section with 305 mm thick fine filetrs complete with fine filters. Velocity across fine filters shall not exceed 500FPM. Filters shall have efficiency not less than 99% down to 3 Microns (EU-7/MERV-13). Filter material shall be non combustible type.
D. Coil Section : Coil section with 6 row (3+3) deep chilled water cooling coil/ DX cooling coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge SS-304 duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties. Face velocity across cooling coil shall not exceed 500FPM. - Space Provision for coil to be provided. Drain Pan with drain arrangement to be provided for coil at this stage.
E. Fan Section : Fan Section comprising of belt driven, DIDW Backward curved AMCA certified centrifugal fan with maximum air outlet velocity of 10m/s suitable for required cfm at 70 mm static pressure (Total static of the unit shall be verified by the OEM before the design & supply of the units). Fan & Motor should be mounted over Aluminium channel of suitable thickness and should be isolated from the unit's bottom panel by means of Spring isolators.
F. Motor : TEFC High efficiecny IE-3 class motors suitably designed for VFD with pulley, belt , Guard
G. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 48 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins. ,The AHU shall be with thermal break profile with internal coving section complete with inspection doors, marine light, limit switch and control wiring as required. AHUs shall have access for all parts.necessary vibration Isolation arrangement, noise level shall not exceed 70 dB
22.63.1 | 3000 cfm to 8000 cfm | per cfm | 65 | 6
22.63.2 | more than 8000 cfm to 13000 cfm | per cfm | 62 | 6
22.63.3 | more than 13000 cfm to 18000 cfm | per cfm | 61 | 5.5
22.63.4 | more than 18000 cfm to 23000 cfm | per cfm | 59 | 5
22.63.5 | more than 23000 cfm to 30000 cfm | per cfm | 57 | 5
22.63.6 | more than 30000 cfm to 40000 cfm | per cfm | 55 | 5
22.63.7 | more than 40000 cfm to 50000 cfm | per cfm | 53 | 5
22.64 | Supply of Ceiling Concealed Fan Coil Unit comprising of 3 rows deep chilled water cooling coil, centrifugal blowers, fractional horse power (FHP) motor, synthetic fibre filters, insulated & extended condensate drain pan along with L-type auxillary tray, casing, coil piping connections, condensate drain piping connections & wiring. Fan coil units shall be suitable for operation on 220 +/- 6% Volts, 50Hz, single phase power supply of following sizes & capacities complete as directed by Engineer-in-charge.
22.64.1 | 3.0 TR nominal capacity with 1200 Cfm air quantity. | Each | 26255 | 2344
22.64.2 | 2.5 TR nominal capacity with 1000 Cfm air quantity. | Each | 25135 | 2244
22.64.3 | 2.0 TR nominal capacity with 800 Cfm air quantity. | Each | 20531 | 1833
22.64.4 | 1.5 TR nominal capacity with 600 Cfm air quantity. | Each | 19162 | 1711
22.64.5 | 1.0 TR nominal capacity with 400 Cfm air quantity. | Each | 17296 | 1544
22.65 | Supply of Chilled Water Ceiling Suspended Hydronic Cassette type fan coil unit, four(4) way directional flow, low noise, each complete with two(2) rows of deep chilled water cooling coil, multi-blade centrifugal fan, test reports from National Accreditation Board for Testing and Calibration Laboratories (NABL)/AHRI accerdited lab, electronic air cleaning system, required set of ball valves with & without strainers & 2 way Motorized valve, insulated condensate drain pans with drain pump assembly & drain pump failure alarm, pipe connections through copper pipes, Infra-red remote control, Liquid Crystal Display (LCD), four (4) speed motor , fan four(4) direction air flow, auto swing louver, decorative panel etc., condensation drain connections, All units shall be suitable for 220 +/- 10% Volts, 50 Hz, single phase power supply etc. complete as per specification. The wireless Remote temperature control / thermostat shall have memory back up for set point re- store in case of power failure and re-start. Four(4)hanger rods with required anchoring fasteners, hooks, washers etc.complete as directed by Engineer-in-charge.
22.65.1 | 4.0 TR nominal capacity with 1600 Cfm air quantity. | Each | 37827 | 3377
22.65.2 | 3.5TR nominal capacity with 1400 Cfm air quantity. | Each | 33970 | 30333
22.65.3 | 3.0 TR nominal capacity with 1200 Cfm air quantity. | Each | 31481 | 2811
22.65.4 | 2.5 TR nominal capacity with 1000 Cfm air quantity. | Each | 28495 | 2544
22.65.5 | 2.0 TR nominal capacity with 800 Cfm air quantity. | Each | 26006 | 2322
22.65.6 | 1.5 TR nominal capacity with 600 Cfm air quantity. | Each | 24264 | 2166
22.65.7 | 1.0TR nominal capacity with 400 Cfm air quantity. | Each | 22149 | 1978
22.66 | Supply of High wall Fan Coil Unit comprising of two 2 rows deep chilled water cooling coil, centrifugal blowers, fractional horsepower (FHP) motor , synthetic fibre filters, insulated & extended condensate drain pan, casing, coil piping connections, condensate drain piping connections & wiring. Fan coil units shall be suitable for operation on 220 +/- 6% Volts, 50Hz, single phase power supply of following sizes & capacities.Complete as directed by Engineer-in-charge.
22.66.1 | 2.0 TR nominal capacity with 800 Cfm air quantity. | Each | 29739 | 2655
22.66.2 | 1.5 TR nominal capacity with 600 Cfm air quantity. | Each | 27375 | 2444
22.66.3 | 1.0 TR nominal capacity with 400 Cfm air quantity. | Each | 26628 | 2378
22.67 | Providing, Fixing, Jointing, Testing & Commissioning of Heavy duty MS 'C ' class (Heavy) pipes conforming to IS 3589 / 1239 part-I for chilled water / Condensor water applications including cutting, screwing, welding etc. & forged steel fittings like elbows, tees, tapers, reducer, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, hanger, vibration isolators and nuts bolts including cutting hole and chase in brick walls and making good the same. complete with painting of one coats of Red Oxide and two or more coats of synthetic enamel paint of desired shade (for condensor water only) complete as required. (Pipe to be tested @ 10Kgf/Sqcm for 2 Hrs.).
22.67.1 | 20 mm dia | Mtr. | 344 | 111
22.67.2 | 25 mm dia | Mtr. | 400 | 111
22.67.3 | 32 mm dia | Mtr. | 514 | 139
22.67.4 | 40 mm dia | Mtr. | 598 | 167
22.67.5 | 50 mm dia | Mtr. | 833 | 222
22.67.6 | 65 mm dia | Mtr. | 1062 | 278
22.67.7 | 80 mm dia | Mtr. | 1311 | 333
22.67.8 | 100 mm dia | Mtr. | 1877 | 444
22.67.9 | 150 mm dia | Mtr. | 2771 | 667
22.67.10 | 200 mm dia, 6.0 mm thick | Mtr. | 4160 | 889
22.67.11 | 250 mm dia, 6.35 mm thick | Mtr. | 4382 | 1111
22.67.12 | 300 mm dia., 7.0 mm thick | Mtr. | 6817 | 1333
22.67.13 | 350 mm dia., 8.0 mm thick | Mtr. | 8738 | 1555
22.67.14 | 400 mm dia., 8.0 mm thick | Mtr. | 13270 | 1778
22.68 | Supplying & fixing of Thermal Insulation on Chilled Water Piping with Factory made Self Sleeve Tubes/ Pre cut Sheets of Class 'O' (FM Approved) Closed Cell Elastomeric Rubber Material, Glue, with 7 mil Glass Cloth with 3 coats of anti UV paint for thicknesses of 50/44/38/32 mm. Thermal Conductivity of this material is 0.035w/m.k. and having µ value ≥ 7000.0 - 65 mm dia : 32 mm thick , 80 -100 mm dia : 38 mm thick , 125 - 150 mm dia : 44 mm thick , 150 - 400 mm dia : 50 mm thick. (Up to 100mm dia Self Sleeve tubes &> 100 NB Pre cut sheets. etc. as required.
22.68.1 | 20/ 25 mm dia | Mtr. | 297 | 28
22.68.2 | 32 mm dia | Mtr. | 355 | 39
22.68.3 | 40 mm dia | Mtr. | 439 | 56
22.68.4 | 50 mm Dia. | Mtr. | 470 | 67
22.68.5 | 65 mm dia | Mtr. | 689 | 83
22.68.6 | 80 mm dia | Mtr. | 851 | 111
22.68.7 | 100 mm dia | Mtr. | 1092 | 150
22.68.8 | 150 mm dia | Mtr. | 1540 | 194
22.68.9 | 200 mm dia | Mtr. | 2296 | 278
22.68.10 | 250 mm dia | Mtr. | 2878 | 389
22.68.11 | 300 mm dia | Mtr. | 3499.9972 | 472
22.68.12 | 350 mm dia | Mtr. | 3892 | 528
22.69 | SITC of Air to water Modular type scroll heat Pump 38-40 KW heating capacity comprsing of single/multiple hermetic scroll compressor driven by suitable KW Sq.Cage induction motor complete with Shell and Tube type Condenser duly insulated with 1 inch thick closed cell insulation material, Air cooled evaporator made of copper tubes and aluminium fins , refrigerant piping, Refrigerant R410a and Oil (First Charge), Microprocessor based control panel & accessories etc, DOL starter,suitable for 400 V+/- 10 % 3 Ph 50 Hz supply, Expansion Valve, Microprocessor based automatic and safety controls all mounted on a M.S. frame duly epoxy coated. Air ambient temp. 5 ° C , Hot water inlet temp. 45 ° C , Hot water outlet temp. 50 ° C | Each | 413292 | 16665
22.70. | Supplying and Fixing of PN 1.6 Butterfly Valve (Wafer Type) with S.G Iron Disc and confirming to IS:13095 complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
22.70.1 | 50 mm dia | Each | 2705 | 444
22.70.2 | 65 mm dia | Each | 3152 | 556
22.70.3 | 80 mm dia | Each | 3715 | 667
22.70.4 | 100 mm dia | Each | 4603 | 889
22.70.5 | 150 mm dia | Each | 6966 | 1333
22.70.6 | 200 mm dia Gear Operated | Each | 16023 | 1778
22.70.7 | 250 mm dia Gear Operated | Each | 23990 | 2222
22.70.8 | 300 mm dia Gear Operated | Each | 34428 | 2778
22.70.9 | 350 mm dia Gear Operated | Each | 44414 | 3333
22.70.10 | 400 mm dia Gear Operated | Each | 66867 | 3888
22.71 | Supplying and Fixing of PN 16 Brass/GM Ball valves with screwed end, SS Ball including teflon tape etc. as required.
22.71.1 | 20 mm dia. | Each | 1095 | 111
22.71.2 | 25 mm dia. | Each | 1303 | 111
22.71.3 | 32 mm dia | Each | 2551 | 167
22.71.4 | 40 mm dia | Each | 3234 | 167
22.72 | Supplying and Fixing of PN 16 Cast Iron Dual Plate Wafer Type Check Valve / Non return valve with SS / Bronze flap complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
22.72.1 | 40 mm dia | Each | 4015 | 333
22.72.2 | 50 mm dia | Each | 4385 | 444
22.72.3 | 65 mm dia | Each | 4612 | 556
22.72.4 | 80 mm dia | Each | 5273 | 667
22.72.5 | 100 mm dia | Each | 6683 | 889
22.72.6 | 150 mm dia | Each | 9072 | 1333
22.72.7 | 200 mm dia | Each | 18768 | 1778
22.72.8 | 250 mm dia | Each | 29239 | 2222
22.72.9 | 300 mm dia | Each | 41412 | 2778
22.72.10 | 350 mm dia | Each | 52566 | 3333
22.73 | Supplying and Fixing of PN 16 Flanged Y strainer fabricated out of cast iron body, SS 304 strainer with perforated screen with 3 mm. dia holes in existing MS / GI pipe complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets etc as required of following sizes.
22.73.1 | 40 mm dia | Each | 4261 | 389
22.73.2 | 50 mm dia | Each | 6202 | 444
22.73.3 | 65 mm dia | Each | 7101 | 556
22.73.4 | 80 mm dia | Each | 7772 | 667
22.73.5 | 100 mm dia | Each | 9891 | 889
22.73.6 | 150 mm dia | Each | 19804 | 1333
22.73.7 | 200 mm dia | Each | 34377 | 1778
22.73.8 | 250 mm dia | Each | 51910 | 2222
22.73.9 | 300 mm dia | Each | 75713 | 2778
22.73.10. | 350 mm dia | Each | 112891 | 3333
22.73.11 | 400 mm dia | Each | 140366 | 3888
22.74 | Supplying and Fixing of PN 16 Double regulating screwed balancing valve with nozzle and fabricated out of bronze, etc. as required of following sizes.
22.74.1 | 20 mm | Each | 4532 | 333
22.74.2 | 25 mm | Each | 5080 | 333
22.74.3 | 32 mm | Each | 7460 | 444
22.74.4 | 40 mm | Each | 8553 | 556
22.74.5 | 50 mm | Each | 11318 | 556
22.75 | Supplying and Fixing of PN 16 Cast Iron Double regulating flanged balancing valve with nozzle and hand wheel complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
22.75.1 | 65mm | Each | 18674 | 556
22.75.2 | 80 mm | Each | 21360 | 778
22.75.3 | 100 mm | Each | 33051 | 1111
22.75.4 | 150 mm | Each | 69919 | 1389
22.75.5 | 200 mm | Each | 117239 | 1778
22.75.6 | 250 mm | Each | 174991 | 2222
22.75.7 | 300 mm | Each | 194258 | 2778
22.76 | Providing and Fixing of PN16 Resilient rubber lined single arch vibration eliminators suitable for raw water up to 45 deg. C temperature, working pressure 8.5 Kg/cm2 and test pressure 14 Kg/cm2 to provide relief from stresses at pipe including Matching Flange (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following Sizes.
22.76.1 | 50 mm Dia. x 150 mm Oal | Each | 4568 | 333
22.76.2 | 65 mm Dia. x 150 mm Oal | Each | 5434 | 444
22.76.3 | 80 mm Dia. x 150 mm Oal | Each | 6711 | 556
22.76.4 | 100 mm Dia. x 150 mm Oal | Each | 9062 | 833
22.76.5 | 150 mm Dia. x 150 mm Oal | Each | 12035 | 1111
22.76.6 | 200mm Dia. x 150 mm Oal | Each | 15090 | 1389
22.76.6 | 250mm Dia. x 200 mm Oal | Each | 25290 | 1666
22.76.7 | 300mm Dia. x 200 mm Oal | Each | 28549 | 1944
22.76.8 | 350mm Dia. x 200 mm Oal | Each | 34992 | 2222
22.77 | Supplying and Fixing of PN 16 Brass/GM Ball valves with integral Y strainer, screwed end, SS Ball including teflon tape etc. as required.
22.77.1 | 20 mm | Each | 3214 | 222
22.77.2 | 25 mm | Each | 3826 | 222
22.78 | SITC of PN25 rated threaded end Brass Pressure Independent control valves (PICV) with ON-Off / Modulating actuator including teflon tape etc. as required.
22.78.1 | 15 mm with ON-Off Actuator | Each | 13358 | 222
22.78.2 | 20 mm with ON-Off Actuator | Each | 14073 | 222
22.78.3 | 25 mm with ON-Off Actuator | Each | 14318 | 222
22.78.4 | 32 mm with modulating Actuator | Each | 31833 | 333
22.78.5 | 40 mm with modulating Actuator | Each | 40226 | 333
22.78.6 | 50 mm with modulating Actuator | Each | 41851 | 333
22.79 | SITC of PN25 rated flanged end ductile iron Pressure Independent control valves (PICV) with modulating actuator complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
22.79.1 | 50 mm | Each | 52736 | 1111
22.79.2 | 65 mm | Each | 67555 | 1111
22.79.3 | 80 mm | Each | 71029 | 2222
22.79.4 | 100 mm | Each | 131488 | 2222
22.79.5 | 150 mm | Each | 190387 | 3333
22.80 | SITC of PN16 threaded end two way valves with On - Off / Modulating actuator including teflon tape etc. as required of f following sizes
22.80.1 | 15 mm with ON-Off Actuator | Each | 3195 | 556
22.80.2 | 20 mm with ON-Off Actuator | Each | 3830 | 556
22.80.3 | 25 mm with ON-Off Actuator | Each | 4155 | 556
22.80.4 | 32 mm with modulating Actuator | Each | 13141 | 1111
22.80.5 | 40 mm with modulating Actuator | Each | 16673 | 1111
22.80.6 | 50 mm with modulating Actuator | Each | 19864 | 1666
22.81 | SITC of PN16 flanged end two way valves with modulating actuator complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
22.81.1 | 65 mm | Each | 32743 | 1666
22.81.2 | 80 mm | Each | 37721 | 1666
22.81.3 | 100 mm | Each | 70991 | 2222
22.81.4 | 150 mm | Each | 101040 | 3333
22.82 | S & F of Auto air vent valve complete with socket, ball valve etc. as required. | Each | 1070 | 222.2
22.83 | SITC of AHU temperature controller including making connections etc. as required. | Each | 5223 | 556
22.84 | SITC of FCU Digital thermostate with manual or automatic fan speed , temperature setting including making connections as required. | Each | 4681 | 556
22.85 | Providing & fixing in position 15 mm 'V' shape mercury in glass industrial type thermometer including Making Drilling, socket in Existing MS Pipe Etc. as required. | Each | 1228 | 222
22.86 | Providing & fixing Stainless Steel pressure gauge with dial of 100 mm dia size and range 0 to 20 kg/sq.cm with 3 / 8 " BSP bottom entry , Ball valve , SS Syphon tube all fittings etc, duly calibrated before installation in MKS and FPS units, Accuracy Level +/- 1% including Making Drilling in Existing MS Pipe Etc. as required. | Each | 1745 | 389
22.87 | P & F of Expansion tank, of size 1000mm x 1000 mm x 1000 mm fabricated out of 5 mm thick MS plate construction, duly insulated and complete with 32 mm dia. Outlets for system connection and overflow make up connection, drain connection, drain valve, vent connections, valves and fittings as required, Expansion tank shall be insulatedwith 50 mm thick PUF insulation cladded with 0.80 mm thick aluminium cladding etc. as required. (On existing Foundation) | Each | 49301 | 5555
22.88 | SITC of Paddle type water flow switch with actuation & delay mechanism for sensitivity in the range of 4 to 10 GPM and suitable for installation in HVAC chilled water pipeincluding making connections, making hole in pipe etc. as required. | Each | 1973 | 278
22.89 | SITC of insulated copper / brass connection set for chilled line consisting of ball valve with strainer at inlet, ball valve at outlet, copper connection set with braided pipe flexible connector at in and out at one end etc excluding 2-Way PICV modulating control valve but provision of fixing it as required for smooth functioning of unit. Valves sizes shall be 25 mm up to 2 TR & 32 mm for 2.5 TR & above for chilled water application.
22.89.1 | Up to 2.0 TR | Each | 13411 | 1666
22.89.2 | 2.5 TR to 4.0 TR | Each | 15588 | 1666
22.90 | SITC of circular type Inline fans for ventilation including motor, with forward curved Direc driven SISW fan, motor and drive suitable for 220 ± 10% volts, 1 phase, 50 Hz A.C supply, thermal overload protection, including making connections, ancilliary structure to suspend it from beam/slab, vibration isolator etc. as required of following sizes. (cost of canvass connection to be paid extra )
22.90.1 | 200 cfm to 500 cfm at 15 mm static | per cfm | 11 | 2
22.90.2 | 501 cfm to 1000 cfm at 15 mm static | per cfm | 9 | 2
22.90.3 | 1001 cfm to 1600 cfm at 15 mm static | per cfm | 8 | 1.4
22.91 | SITC of cabinet type(sound insulated casing) Inline fans for ventilation including motor, with forward curved Direc driven DIDW fan, motor and drive suitable for 220 ± 10% volts, 1 phase, 50 Hz A.C supply, thermal overload protection, including making connections, ancilliary structure to suspend it from beam/slab, vibration isolator etc. as required of following sizes. (cost of canvass connection to be paid extra ) etc .as required.
22.91.1 | 501 cfm to 1000 cfm at 15 mm static | per cfm | 14 | 2.2
22.91.2 | 1001 cfm to 1500 cfm at 15 mm static | per cfm | 13 | 1.9
22.91.3 | 1501 cfm to 2000 cfm at 20 mm static | per cfm | 12 | 1.7
22.91.4 | 2001 cfm to 2500 cfm at 20 mm static | per cfm | 11 | 1.7
22.91.5 | 2501 cfm to 3000 cfm at 20 mm static | per cfm | 10 | 1.7
22.92 | SITC of AMCA Certified (For Air and Sound Performance) tube axial flow fan in standard M.S.contruction. Entire fan model & AMCA Seal shall apear in techncial submittal of fan. All the fans are synthetic enamelled panited/hot dip galvanized with minimum 220 GSM Zinc Coating and complete with bird screen at inlet. The electric motor coupler shall be squirrel cage induction motor (IE-2 type) confirming to IS - 325 IP55 with class `H' insulation. Motor shall be of high temperature resistance "Class H Smoke Spill" 250° C for 2 hrs. Fan shall be EN 12101-3 Certified & CE/UL Listed for high temprature. Fan efficiency should not be less than 70 %, noise level should not be more than 80 db @ 3 m distance when measured in hemisperical reverberant room conditions for Normal mode Fans and noise level should not be more than 90 db @ 3 m distance when measured in hemisperical reverberant room conditions for Emergency mode Fans. Fan shall have all provision for start on emergancy signal from fire alarm panel including ancilliary structure to suspend it from beam/slab, vibration isolator etc. as required of following sizes. (cost of canvass connection to be paid extra )
22.92.1 | 5000 cfm to 15000 cfm with static 30 mm | per cfm | 8 | 1.7
22.92.2 | 15001 cfm to 25000 cfm with static 30 mm | per cfm | 7 | 1.7
22.92.3 | 25001 cfm to 40000 cfm with static 30 mm | per cfm | 6 | 1.4
22.93 | Supply, Installation, Testing & Commisioning of AMCA Certified (For Air and Sound Performance) tube axial flow fans of different capacities in standard GI/M.S. contruction as mentioned below. Entire fan model and AMCA Seal shall apear in techncial submittal of fan. All the fans shall be synthetic enamel painted/ hot dip galvanized with minimum 220 GSM Zinc Coating and complete with bird screen at fan inlet. The electric motor coupler shall be IE-03 squirrel cage induction type conforming to IS-325, IP-55 rated with class `F' insulation. Fan efficiency should not be less than 65%, and noise level should not be more than 70 db @ 3 m distance when measured under hemisperical reverberant room conditions. Quoted price shall be inclusive of sound attenuator at the outlet/inlet of the fan. Fans mentioned as outdoor type shall be good for outdoor installation with proper cowl including ancilliary structure to suspend it from beam/slab, vibration isolator etc. as required of following sizes. (cost of canvass connection & cowl to be paid extra )
22.93.1 | 5000 cfm to 15000 cfm with static 30 mm | per cfm | 7 | 1.7
22.93.2 | 15001 cfm to 25000 cfm with static 30 mm | per cfm | 6 | 1.7
22.93.3 | 25001 cfm to 40000 cfm with static 30 mm | per cfm | 5 | 1.7
22.94 | Providing & Fixing of Dual Speed Ductless Ventilation / Jet fans as per specifications for normal ventilation suitable for Normal ventilation and Smoke Extraction application. The complete fan assembly with all supporting, mounting structural frame, Casing, impeller, tranformer, starter & motor (the entire motor fan,controller etc., as a full package) shall need to be imported from manufacturer and certified as tested for 300 Deg C for 2 hours operation. The jet Impulse fans 355mm dia Fan is with mounting arrangements. Fan is capable of running at 300Deg. C at least for 2 Hours.Along with necessary protective grill & Structure work. Each fan shall be complete with Dual speed motor. Casing shall be made Galvanized Aluminum. The Motor shall be run on the electrical power suitable for 50Hz. including ancilliary structure to suspend it from beam/slab, vibration isolator etc. as required of following sizes.
22.94.1 | 2000 CFM Normal Mode/ 4000 CFM Fire Mode | Each | 67258 | 2778
22.94.2 | 3500 CFM Normal Mode/ 7000 CFM Fire Mode | Each | 87645 | 3333
22.94.3 | 5000 CFM Normal Mode/ 10000 CFM Fire Mode | Each | 103601 | 4444
22.95 | Providing & Fixing of Control Panel with dual speed starters to operate 2 No. Fans with IP based 32 bit microprocessor based standalone programmable controller with real time clock and required IO points housed in powder coated MS enclosure including internal wiring, relays, connector strip, CT, MCB etc, as required. | Each | 43235 | 5555
22.96 | Providing and fixing of IP-30 sensor with response time >/= 45 Sec. for continuous monitoring of CO and radicals concentration in ambient air, measuring range: 0-400 ppm , self calibration function, including mounting accessories etc. as required. | Each | 10244 | 556
22.97 | S & F of SMPS 24 V with metal enclosure as required | Each | 1514 | 222
22.98 | S & layiing 1.0 Sq.mm x 8 core copper control cable from FCU to Thermostate in existing conduit as required. | Mtr. | 124 | 17
22.99 | Supplying & fixing of Thermal Insulation on Chilled Water line Butterfly valves / Sluice valves / NRV / PICV / Y strainer / Two Way Valve / Balancing valve with Class 'O' (FM Approved) Closed Cell Elastomeric Rubber Material with 7 mil Glass Cloth with 3 coats of anti UV paint for thicknesses of 32 mm. Thermal Conductivity of this material is 0.035w/m.k. and having µ value ≥ 7000. etc. as required.
22.99.1 | 20 mm | Each | 273 | 111
22.99.2 | 25 mm | Each | 326 | 111
22.99.3 | 32 mm | Each | 408 | 139
22.99.4 | 40 mm | Each | 490 | 167
22.99.5 | 50 mm | Each | 598.9956 | 222
22.99.6 | 65 mm | Each | 708 | 278
22.99.7 | 80 mm | Each | 872 | 333
22.99.8 | 100 mm | Each | 1090 | 444
22.99.9 | 150 mm | Each | 1417 | 556
22.99.10 | 200 mm | Each | 1854 | 778
22.99.11 | 250 mm | Each | 2292 | 1000
22.99.12 | 300 mm | Each | 2726 | 1111
22.99.13 | 350 mm | Each | 3217 | 1333
22.100. | SITC of modular and portable water softner with LCD control panel based on automatic regeneration technology and microprocessor-controlled method to convert hard water into soft water, the hard water should pass through 5 stages of regeneration - normal, backwash, recharging, flushing and brine refill with no manual intervention or technical help. Water softened before regeneration shall be 5500 Liters with resin volume of 28 Liters. It shall be used to to supply soft water in chilled water expansion tank. | Each | 92246 | 5555
22.101 | SITC of the following capacities CS Closed Expansion tank with full acceptance Factor pre-charged bladder-type pressure vessels. The tank shall be designed to absorb the expansion forces of heating/cooling system water while maintaining proper system pressurization under varying operating conditions. The heavy duty bladder should contain system water thereby eliminating tank corrosion and water logging problems. The system should include PRV and Airvent also. And complete as per technical specification. Tank shall be selected for PN-16 rating
22.101.1 | 500 Ltr. | Each | 195869 | 8888
22.101.2 | 1000 Ltr. | Each | 266084 | 11110
22.102 | SITC of centrifugal/ coalescence type air separator for required pipe size. The unit shall inlet and outlet connections tangential to the vessel shell. The unit shall have an internal stainless steel collector tube with 5/32” (4mm) diameter perforations and 63% open area designed to direct accumulated air to the compression tank on an air control system or an air vent on an air elimination via an NPT vent connection at top of the unit. | Each | 101879 | 5555
22.103 | Supply, Installing, Testing and commissioning of Pressurizing unit consisting of Inline vertical multistage, centrifugal clear water pumps ( 1W+1S) with S.S. 304 casing, S.S. 304 impeller and S.S. 316 shaft, CI Base,TEFC motor (with mechanical seal) with control panel with duty cycling and dry run protection and set of accessories such as pressure transmitter, suction and discharge pipe manifolds, pressure gauges, valves etc. conforming to the specifications. The make up tank location should be at least 1 meter above the pump level.
| The unit shall include Control panel, Set of accessories such as pressure switches, suction and discharge pipe manifolds, pressure gauges, valves etc. | Each | 173872 | 3888
22.104 | S & F of eye Ball diffuser Made out from heavy duty alluminium sheet, finished with powder Coated with pivoting movement of +/-20 degree. Of following Nominal Dia. As required.
22.104.1 | With two Flap Butterfly Damper
22.104.1.1 | 150 mm Dia. | Each | 1922 | 222
22.104.1.2 | 200 mm Dia. | Each | 2373 | 333
22.104.1.3 | 300 mm Dia. | Each | 3275 | 556
22.104.1.4 | 400 mm Dia. | Each | 4238 | 556
22.104.2 | Without Damper
22.104.2.1 | 150 mm Dia. | Each | 1582 | 222
22.104.2.2 | 200 mm Dia. | Each | 2033 | 333
22.104.2.3 | 300 mm Dia. | Each | 2822 | 556
22.104.2.4 | 400 mm Dia. | Each | 3615 | 556
22.105 | Supply , Installation, Testing and Comissioning of IS:1475 marked self contained drinking water cooler with hermetically sealed compressor,non CFC refrigerent suitable for operation on 230V/1pH/50Hz AC supply,Full stainless steel (SS304)body (0.8 mm thick) and tank (0.5 mm thick) , stainless steel water tray,minimum two nos Brass Chrome plated faucets and suitable drainage system complete in all respect with required height MS fabricated and Painted Angle iron frame ( Cost of frame to be paid Extra )complete in all respect of the following capacity.
22.105.1 | cooling capacity 150 Ltr./Hr. and storage capacity 150 Ltrs | job | 66038 | 3145
22.105.2 | cooling capacity 60 Ltr./Hr. and storage capacity 120 Ltrs | job | 55924 | 2663
22.105.3 | cooling capacity 40 Ltr./Hr. and storage capacity 80 Ltrs | job | 50570 | 2408
22.106 | Providing & Fixing of 26 SWG thick Aluminium sheet cladding on existing refrigerant copper pipe /insulated chiller pipe or any other surface with nut & bolts complete as required. | Sqmtr | 488 | 23
22.107 | Providing & Fixing of BIS certified Oil filled radiator having following fins with temperature control setting sound free operation with minimum 1 year warranty & temperature setting, Rated Voltage:-230 V, Rated Wattage:-2400 W made out from CRCA sheet with powder coating, tubular type element castor wheel, 1.5 mtr PVC power cord along with 16 Amp plug top. net weight should not be less then 12 Kg and minimum dimensions are 520 X 165 X 710mm complete in all respect. NABL accredeated / appropriated lab testing reports with OEM certificate must submitted to engineer in charge.
22.107.1 | 9 Fins | Each | 13684 | 652
22.107.2 | 11 Fins | Each | 15944 | 759
22.107.3 | 13 Fins | Each | 17491 | 833
22.108 | SITC of Air Curtain made out from Stainless steel 304, 90 CM width, suiatble for working 230 +-10 % with low & high voltage cutoff & 50 Hz frequency, single phase AC supply with maximum air velocity 12-14 m/s and noise level not more then 55 db including power cable and stand including fixing with T&P & Labour etc as required | Each | 23798 | 1133
22.109 | SITC of Air Curtain made out from Stainless steel 304, 120 CM width, suiatble for working 230 +-10 % with low & high voltage cutoff & 50 Hz frequency, single phase AC supply with maximum air velocity 18-22 m/s and noise level not more then 55 db including power cable and stand including fixing with T&P & Labour etc as required | Each | 30937 | 1473
22.110. | SITC of RO water system with Filteration stages = Particilate filter- Membrane life enhancer filter- sediment filter- pre carbon filter- RO membrane filter- post carbon filter. Input power rating -230V AC, 50Hz, percentage of rejection TDS-90% or better, having following features (a) Double purification by RO with ESS or latest technology with TDS indicator. (b) Spin welded RO membrane housing to prevent tempering. (c) Push fit component for leak proof performance. (d) Fully automatic operation with auto start and auto off. (e) SS/ABS construction for corrosion free lifespan. (f) Equally suitable for water from all borewells, overhead storage tanks, water tankers and even municipal taps. (g) RO membrane flushing - Auto flush@ every start, every stop and every one hour of working for one minute, complete in all respect with following capacity.
22.110.1 | Purification capacity - 50LPH, duty cycle 270-500 liters/day | Each | 49928 | 2333
22.110.2 | Purification capacity - 25LPH, duty cycle 170-250 liters/day | Each | 28530 | 1333
22.110.3 | Production capacity- 15 LPH, Water storage capacity 8 ltr | Each | 16048 | 750
22.111 | Supply,installation testing & commissioning of skid mounted Reverse Osmosis System of following output capacity designed at a minimum Flux at inlet and necessary of minimum 60-70% recovery, complete as required with the following items: - R.O plant at Terrace Level for Drinking purpose (Cost of Raw water tank and Product water Tank ,Shed for plant, plumbing and 3 phase supply arrangements to be paid extra)
22.111.1 | RO plant 250 LPH (Skid mounted)
Filter Feed Pump 1 Nos. -Motor Rating 0.5 HP, MOC- CastIron ,Capacity 1000.LPH .
Pressure Sand Filter 1 Nos.- vessel made by FRP, sand +support bed media, single-multiport valve,Capacity 1000 LPH.
Activated Carbon Filter 1 Nos.- vessel made by FRP, Carbon+Support Bed media, single multiport valve,Capacity 1000 LPH.
Antiscalant Dosing System 1 Nos.- Electro-Magnetic Type, MOC- HDPE, 4 kg/c m2 Operating Pressure & Capicity 1.5LPH.
Dosing Tank 1 Nos.- MOC Of Tank-HDPE & Capacity OfDosing Tanks 50 Lit.
Micron Cartridge Filter 1 Nos.-MOC of Housing-ABS & Cartridge-PP, Capacity 1000 LPH, RATING 5 Micron.
High Pressure Pump 1 Nos.- Capacity 1000 LPH , VerticalMultistage Type Pump , MOC- SS 304
Membranes 1 Nos.
UV System 1 Nos.- Capacity 250LPH
Instrumentation - 3 Nos. Of Pressure gauges, Pressureswitches 2 Nos., Conductivity Meter (Inbuilt in panel)1 Nos. online Type, Level Switch 2 Nos. ,Flow Indicator 1 Nos.
Control Panel 1 Nos.
| ICPW 1 Lot.-Low Pressure / High Pressure - UPVC | Set | 314049 | 14675
22.111.2 | RO plant 500 LPH (Skid mounted)
Filter Feed Pump 1 Nos. - Horizontal Centrifugal Type , MOC-Cast Iron , Single Phase,220V, 50 Hz Supply , 1100LPH Flow , Head 25mwc.
Pressure Sand Filter 1 Nos.-Size- 10” x 54” vessel made by Polyglass, sand + support bed media, manual top-mounted multiport valve, UPVC Sch. 40 frontal piping ,OperatingCapacity 1100LPH.
Activated Carbon Filter 1 Nos.-Size- 10” x 54” vessel made by Polyglass, Activated Carbon +Support Bed media, manual top- mounted multiport valve, UPVC Sch. 40 frontal piping ,OperatingCapacity 1100LPH.
Antiscalant Dosing System 1 Nos.- ElectronicDiaphragm Type, MOC Of Pump-PP, Capacity Of Dosing Pump 0-1.5LPH & 2.5 kg/c m2 Operating Pressure.
Dosing Tank 1 Nos.- MOC Of Tank-LLDPE & Capacity OfDosing Tanks 60 Lit.
Micron Cartridge Filter 1 Nos.-MOC of Housing-ABS & Cartridge-PP, Operating Capacity 1100LPH, RATING 5 Micron.
High Pressure Pump 1 Nos.- 1100LPH Capacity With 120Mtr. Head, Vertical Centrifugal Multistage Type , MOC- SS 304(wetted parts) , 3 Phase Supply
Pressure Vessel 2 Nos.- MOC-FRP With 4" Diameter
Membranes 2 Nos. -Size- 4”, TFC Polyamide Type
UV System 1 Nos.- MOC - SS 304, Capacity 500LPH
Instrumentation - 1Set Of Pressure gauges, 1Set OfRotameter, Pressure switches for Low Pressure 0.5-5 kg/c m2 Range 1 Nos. & High Pressure 2-25 kg/c m2 Range 1 Nos. , Conductivity Meter (Inbuilt in panel)1 Nos. online Type, 0 – 200 µSiemens/cm Range , Level Switch 2 Nos.
Control Panel 1 Nos. -Microprocessorbased control Type Semi-Automatic Operation
| ICPW 1 Lot.-Low Pressure / High Pressure - UPVC Sch. 40,Outlet flange of raw water pump to outlet flange of UVsystem(piping terminated on skid) | Set | 385589 | 18018
22.111.3 | RO plant 1000 LPH (Skid mounted)
Filter Feed Pump 1 Nos. -Centrifugal Mono-block Type , MOC-Cast Iron ,Capacity 2.0 m3/hr @ 25 mwc.
Pressure Sand Filter 1 Nos.-Size- 16” x 25” vessel made by Polyglass, sand + support bed media, manual multiportvalve,Capacity 2.0 m3/hr.
Activated Carbon Filter 1 Nos.-Size- 16” x 25” vessel made by Polyglass, Activated Carbon +Support Bed media, manualmultiport valve,Capacity 2.0 m3/hr.
Antiscalant Dosing System 1 Nos.- Electro-Magnetic Type, MOC- HDPE, 2.5 kg/c m2 Operating Pressure & Capicity 0-6LPH.
Dosing Tank 1 Nos.- MOC Of Tank-HDPE & Capacity OfDosing Tanks 50 Lit.
Micron Cartridge Filter 1 Nos.-MOC of Housing-ABS & Cartridge-PP, Capacity 2.0 m3/hr, RATING 5 Micron.
High Pressure Pump 1 Nos.- Capacity 2.22 m3/hr , VerticalMultistage Type Pump , MOC- SS 304
Membranes 4 Nos.
UV System 1 Nos.- Capacity 1000LPH
Instrumentation - 1Set Of Pressure gauges, Pressure switches 2 Nos., Conductivity Meter (Inbuilt in panel)1 Nos. online Type,Level Switch 1 Lot. ,Flow Indicator 1 Lot.
Control Panel 1 Nos.
| ICPW 1 Lot.-Low Pressure / High Pressure - UPVC | Set | 542008 | 25328
22.112 | Supply and Fixing of Desert Cooler having cooling capacity of 5000 cum/hr., approx. size of cooler is 28"x28"x38" and having tank of 9" height with 20" 1400 rpm heavy duty fan motor and required size of submersible pump and all other required accessories. Cooler should be made of 18 SWG GI sheet for tank and remaining cooler body should be of 20 SWG GI sheet, grill of size 22"x25" including required size angle iron stand duly painted with 2 coats of red oxide and one coat of enamel paint complete in all respect as required. | Each | 12688 | 222

## ch 23 Substation Equipments.
Chapter E - 23
Substation Equipments
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
23.1 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 11/0.433KV Delta-Star Connected, Vector Group Dyn 11, ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-1, including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve(above 800 Kva) Suitable size HT cable box, LT cable box or Busduct adaptor box, Off -LTC ( +5% to - 7.5% in steps of 2.5 %), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, Unidirectional rollers for rating upto 800 kva & bi- directional above 800 Kva rollers with locking arrangement etc. as required. Factory Tests: The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM's own lab and same shall be witnessed by Department engineer. Site Tests: Following tests shall be carried out on each transformer at site by OEM enginer in presence of department's site engineer:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. Transformer shall also be tested in CTL of discom before charging & complete installaion must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspectorate office charges shall be reimbursed to the contractor)
Note :Manufacturer's testing laboratory should be certified by NABL and have an in house core cutting facility to ensure proper control & monitoring of quality. This is crutial to prevent the mixing of prime core materials with Second grade or defective materials. The core should be constructed from high grade, non ageing, PRIME GRADE CRGO steel with M4 Grade or Better, using silicon steel laminations, and should be of boltless design. The core and coil assembly should be undergo drying process using a highly efficient vacuum drying autoclave to remove moisture through heating and drying.
23.1.1 | 500 KVA with % Impedance 4.5 | Set | 1467562 | 41121
23.1.2 | 630 KVA with % Impedance 4.5 | Set | 1632337 | 45829
23.1.3 | 800 KVA with % Impedance 5.0 | Set | 1908698 | 36052
23.1.4 | 1000 KVA with % Impedance 5.0 | Set | 2232110 | 42162
23.1.5 | 1250 KVA with % Impedance 5.0 | Set | 2503527 | 47273
23.1.6 | 1600 KVA with % Impedance 6.25 | Set | 2829717 | 53328
23.1.7 | 2000 KVA with % Impedance 6.25 | Set | 3187681 | 59994
23.1.8 | 2500 KVA with % Impedance 6.25 | Set | 3539979 | 66660
23.2 | S I T C of star rated Aluminium wound distribution Transformer of following rating 11/0.433KV Delta-Star Connected, Vector Group Dyn 11,ONAN Cooled & as per BEE star - 1 ( Correspnding level as per BIS amended upto date of receipt of tender) & BIS approved as per IS 2026- 1977 & losses as defined as per 2014 (Fourth Revision) Level-1 including standard accessories like conservator, silica gel breather, radiator, fins, HT cable box & LT cable boxes, temperature rise in winding/oil 35-40 degree C upto 200 KVA & 40-45 degree C for above 200 KVA, ISI marked drain valve, Dial type Temperature gauge, first filling of transformer oil as per IS :335-1953, Epoxy based paint, undirectional rollers as required including carrying of pre-commission Testing & Charging of Transformer complete in all respect . Factory Tests : The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) in OEM's own lab and same shall be witnessed by Department engineer. Site Tests : Following tests shall be carried out on each transformer at site by OEM engineer in presence of department's site engineer:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. Transformer shall be tested from CTL of discom before charging of transformer & complete installaion must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)
Note :Manufacturer's testing laboratory should be certified by NABL and have an in house core cutting facility to ensure proper control & monitoring of quality. This is crutial to prevent the mixing of prime core materials with Second grade or defective materials. The core should be constructed from high grade, non ageing, PRIME GRADE CRGO steel with M4 Grade or Better, using silicon steel laminations, and should be of boltless design. The core and coil assembly should be undergo drying process using a highly efficient vacuum drying autoclave to remove moisture through heating and drying.
23.2.1 | 63 KVA with % impedance 4.5 | Set | 184259 | 8610
23.2.2 | 100 KVA with % impedance 4.5 | Set | 231810 | 10832
23.2.3 | 160KVA with % impedance 4.5 | Set | 297193 | 13888
23.2.4 | 200 KVA with % impedance 4.5 | Set | 386350 | 18054
23.2.5 | 250 KVA with Off -LTC (+5% to - 10% @ 2.5%) with % impedance 4.5 | Set | 427957 | 19998
23.2.6 | 315 KVA with Off -LTC (+5% to - 10% @ 2.5%) with % impedance 4.5 | Set | 606606 | 17332
23.2.7 | 400 KVA with Off -LTC (+5% to - 10% @ 2.5%) with % impedance 4.5 | Set | 653268 | 18665
23.2.8 | 500 KVA with Off -LTC (+5% to - 10% @ 2.5%) % Impedance 4.5 | Set | 793254 | 22664
23.2.9 | 630 KVA with Off -LTC (+5% to - 10% @ 2.5%) % Impedance 4.5 | Set | 904076 | 22664
23.2.10 | 800 KVA with Off -LTC (+5% to - 10% @ 2.5%) % Impedance 5.0 | Set | 1108223 | 31664
23.3 | SITC of Marshalling box fabricated out of 2.0 mm thick sheet steel, provided with water tight hinged doors with padlock arrangement, neoprene gasket all around door to make enclosure water and dust proof (IP-55). Space Heater, Illumination lamp, 5A switch & Socket, MCB, Viewing window, detachable gland plate completely wired, ready for external connections at the terminal blocks. All wirings shall be carried out with 1100 V grade PVC insulated stranded conductors. Power circuits if any shall be wired with stranded copper conductors of adequate sizes to suit the rated current. The minimum size shall be 2.5 sq.mm. Control, alarm and indication circuits, shall be wired with stranded copper conductor of sizes not smaller than 1.5 sq. mm. CT circuits shall be wired with stranded copper conductor of size not smaller than 4 sq.mm. including 150 mm dia. Winding temperature indicator with A&T contacts, 150 mm dia. Oil temperature indicator with A&T contacts , 150 mm dia. Magnetic Oil level Gauge ( MOG) with alarm contact, double float type Buchholz relay with isolating valves on both sides and as per IS: 3637 with A&T Contacts etc. as required. | Set | 89871 | 4200
23.4 | Add Extra for On load tap changer (OLTC) (+5% to - 15% @ 1.25%) and Remote tap changer control (RTCC) panel with Automatic voltage regulator (AVR) in place of Off circuit tap chaner (OFTC) for 11/0.433 KV Transformer | Set | 356631 | 16665
23.5 | Supply & Installation of D.P. Structure With AIR BREAK SWITCH having following specifications A, B, C, D, E.
A) Double pole structure on 2 no ISMB ( I beam ) of size 150 x 75 mm x 8 mm, 9 mtr length using MS channel each of size 100 mm x 50 mm x 2500 mm ( 3 No. ) and of size 75 mm x 40 mm x 2500 (4 No.) mm complete in all respect with nuts, springs washers, clamps as required.
B) Off load type gang operated 3-pole horizontal flute type switch suitable for 11KV ; 400A ,3-ø, central post rotating double break isolator complete with MS hardware , copper moving & fixed contact ,assembly of 9 nos pin insulator , 25 mm ‘B’ class GI pipe of suitable length for operation.
C) 3nos Vertical / Horizontal mounted 11kv horn gap fuse set /drop out 11kv barrel fuses mounted on 6no pin insulators
D) 3 piece non linear resistor type. lighting arrestor of approved make suitable for 3 wire, 11kv Overhead line with rated voltage of 9kv rms & nominal discharge current rating of 5 kA & complete with galvanized clamping arrangement GI bolts, nuts, washer etc as required.
| E) 3 no 11kv ACSR conductors mounted on pin type insulators as required. | Set | 87933 | 16665
23.6 | SITC of 11kV 630 Amps 21KA for 3 Sec. SF6 insulated, outdoor duty (IP54) , Extensible / Non extensible type Ring main unit (RMU) manually operated in combination of VCB modules and Load Break switch consisting of Copper busbar in SF6 insulated stainless steel Outdoor enclosure of thickness of 2 mm and tank of stainless steel Outdoor enclosure of thickness 3mm with manometer. The HV switchgear and control gear should be confirming to IEC-62271-100, IEC-62271-200-2003 & IEC-60694-1996. The RMU should be internal arc tested for 21KA for 1Second with IAC-AFL classification for both Cable chamber and gas tank as per IEC 62271-200 and LBS to be rated for class E3 as per IEC 62271 - 103. Vacum Interrupter should be same as used during type test of RMU. Each feeder of RMU should have voltage presence indicator. and VCB feeder should consist of 1 no. microprocessor based Self powered numerical relay with over Current/ earth fault & short circuit protection with each VCB feeder, 3 Nos. Protection CT shall be of Burden 2.5VA, ratio 50/1A, Class of Accuracy class 5P10 for O/C and E/F protection for each VCB. Load break switch feeder shall have Fault Passage indicator, Right angle boots for all the feeder Modules, Remote trip, Emergency Stop, Cable cover interlocking, Trasnformer protection tapo card etc. All the type test certificates as per IEC and CEA from Third party NABL / CPRI / ERDA accrediated lab to be submitted. (Cost of RCC Foundation / Steel Structure to be paid Extra)
23.6.1 | Non Extensible 3 way RMU with 1 no. VCB & 2 No. Load Break Switch | Set | 379129 | 10832
23.6.2 | Extensible 3 way RMU with 1 no. VCB & 2 No. Load Break Switch | Set | 402460 | 11499
23.6.3 | Extensible 2 way RMU with 1 no. VCB & 1 No. Load Break Switch | Set | 332467 | 9499
23.6.4 | Non Extensible 1 way RMU with 1 no. VCB & Direct Cable Entry | Set | 297470 | 8499
23.6.5 | Extensible 1 way RMU with 1 No. VCB & Direct Cable Entry. | Set | 309136 | 8832
23.6.6 | Coupling Assembly to connect two different RMUs. | Set | 31502 | 1472
23.7 | SITC of Indoor Type Floor mounted metal clad 11 KV, 630 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) Panel having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec. It must be Fabricated with High quality Aluminium-Zinc (Aluzinc) coated sheet steel / CRCA sheet 2.0 mm thick as per IEC 62271-1,100,200 Standard in VCB Manufacturer's own Factory . with AFLR clasification totally enclosed with Aluminium bus bar of 630 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 3 vaccum interrupters (VCB manufacturer's own make) , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker ,interconnected with HT sleeve bus bar of 630 Amps or as per type test design , Basic Insulation level (BIL) : 28KV (RMS) / 75KV (Peak) and Altitude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. Factory Tests of VCB panel as per Routine test prescribed in BIS in it’s own Manufacturing facility (Cost of RCC Foundation / Steel Structure to be paid Extra).
23.7.1 | Incoming Cum Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : suitable ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA - PT Ratio: 11KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of AC Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. | Set | 746592 | 21331
23.7.2 | Incoming Panel comprising of following: - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : Suitable Ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA. - PT Ratio: 11KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. | Set | 729094 | 20831
23.7.3 | Outgoing Panel comprising of following: - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Suitable Ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) | Set | 694097 | 19831
23.7.4 | Bus Coupler Panel comprising of following: -VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Space heaters - Power Pack (230V AC- 110V DC) | Set | 653268 | 18665
23.8 | SITC of Indoor Type Floor mounted metal clad 11 KV, 630 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) Panel having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec Panel Fabricated by System Integrator of VCB Manufacturer as per IEC 62271-1,100,200 Standard made from Powder painted pre-fabricated, 2.0 mm thick CRCA sheet steel, totally enclosed with Aluminium bus bar of 630 Amps for each phase, flush front, Horizontal isolation, Horizontal draw out type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assembly of 3 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker ,interconnected with HT sleeve bus bar of 630 Amps or as per type test design , Basic Insulation level (BIL) : 28KV (RMS) / 75KV (Peak) and altitude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. Factory Tests of VCB panel as per Routine test prescribed in BIS in it’s own Manufacturing facility.(Cost of RCC Foundation / Steel Structure to be paid Extra).
23.8.1 | Incoming Cum Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : Suitable Ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA. - PT Ratio: 11KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. | Set | 536613 | 15332
23.8.2 | Incoming Panel comprising of following: - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : Suitable ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA. - PT Ratio: 11KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. | Set | 519115 | 14832
23.8.3 | Outgoing Panel comprising of following: - VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : suitable Ratio as required, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA . - Numerical relay having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) | Set | 501617 | 14332
23.8.4 | Bus Coupler Panel comprising of following: -VCB 630 Amps . Vaccum Interrupter of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Space heaters - Power Pack (230V AC- 110V DC) | Set | 466620 | 13332
23.9 | SITC of 11 kV Factory Assembled Outdoor Package Sub-Station (PSS), Design and manufactured by the OEM. The PSS shall comprise of RMU, LT Switchgear (ACB), Transformer, etc. with a requirement that at least two of these components are of the same make as that of PSS. The PSS should consist of following sections and their specifications as per A, B, C, D & E
A) HT Compartment: Ring Main Unit 11kV 630 Amps 21KA for 3 Sec. SF6 insulated, non-extensible, Ring main unit consisting of 2 nos. manually operated Load Break Switch and 1 Nos. 630 Amp Vacuum Circuit Breaker (manually operated and Operating Sequence of VCB Should be O-0.3S-CO-3Min-CO.or as per type test design) with Copper busbar in SF6 insulated stainless steel Outdoor enclosure of thickness of 2 mm and tank of stainless steel Outdoor enclosure of thickness 3mm with manometer. Interconnection between HT switchgear and transformer by Suitable Sized Aluminium un-armoured HT XLPE Cable. The HV switchgear and control gear should be confirming to IEC-62271-100, IEC-62271-200-2003 & IEC-60694-1996. The Gas tank of the RMU should be internal arc tested for 20KA for 1 Second. VI should be of make for which type test was done. - 1 no. microprocessor based Self powered numerical relay with over Current/ earth fault & short circuit protection with each VCB feeder. - 3 Nos. Protection CT shall be of Burden 2.5VA, ratio 50/1A, Class of Accuracy class 5P10 for O/C and E/F protection for each VCB feeder - 1 No. Manometer - 1 No. Fault Passage Indicator for each Load Break switch.
B) Transformer: 11kV/433V, 3phase,50 HZ, Copper wound Dry Type / Hermatically sealed oil type step down transformer having delta connection on primary side and star connection on secondary side complete with all modern fitting as given in the specification , off load tap changer (-10% +5% in the step of 2.5%) etc. as required with losses as per ECSBC 2024 Standards , Class H with 115 Deg temperature rise allowed . - One No. Winding Temperature Indicator with Alarm and trip Contacts
C) LV Compartment: Incoming cum Outgoing with One number manual spring charged drawout type 4 pole 415V ACB with breaking capacity 50KA with Ics = Icu = Icw (1 sec) = 50KA with microprocessor release for over current, earth fault & short circuit protections. Interconnection between Transformer & LT switchgear using Aluminum Bus bars of ACB Current rating with heat shrinkable colored sleeves.
D) The Outdoor enclosure shall be made of 2.0 mm for Load bearing and 1.5 mm mm thickness for Non load bearing part, Galvanized Sheet Steel tropicalised to meet Indian weather conditions including all the partition Sheets & doors. The enclosure base shall be of 4.0 mm thickness Hot Dip Galvanized Sheet Steel. The entire Package Substation shall be Factory Assemble & Factory Fitted. The enclosure shall have IP54 degree of protection for HT & LT switchgear compartment IP-23 degree of protection for Transformer compartment. The Enclosure should be type tested for Internal Arc fault test to the tune of at least 21 KA for 1 second adhering to as per latest IEC 62271- 202. The offered enclosure should be type tested for K10 class temparature raise. TTR to be submitted. The enclosure exterior shall be powder coated. The compartment illumination lamp with door operated switch shall be provided for MV & LV compartment. Internal earthing connections by using 50x6mm GI Strips. Specifications of RMU, Transformer and ACB will be as per respective chapter of BSR
E) OEM of PSS shall provide Type test certificates for the RMU, Transformer & LT Switchgear. .
Factory Tests: All test shall be conducted as per the QAP of OEM at the Manufacturing facility and same shall be witnessed by departmental Engineers.
Note: Cost of RCC Foundation / Steel Structure to be paid Extra.
23.9.1 | Transformer Capacity 250 KVA, ACB Rating 630 Amps. | Set | 2706396 | 77326
23.9.2 | Transformer Capacity 500 KVA, ACB Rating 1000 Amps. | Set | 3406326 | 97324
23.9.3 | Transformer Capacity 630 KVA, ACB Rating 1250 Amps. | Set | 3849615 | 103389
23.9.4 | Transformer Capacity 750 KVA, ACB Rating 1600 Amps. | Set | 4222911 | 120655
23.9.5 | Transformer Capacity 1000 KVA, ACB Rating 2000 Amps. | Set | 4724528 | 134987
23.10. | SITC of battery bank of min 150 AH capacity comprising SMF/VRLA batteries, FCBC ( Float cum boost charger)suitable for 415V +/-10%, 50 Hz , 1-ǿ / 3 -ǿ Input & 24/ 48 /110 V DC Output Natural Cooled, free standing in Sheet Steel enclosure,SCR controlled , regulation +/-1% , Efficiency > 75% on FLAC/ DC Instruments, Selector Switch ,Built in DC Distribution Board (6 No MCB), indication , control as required. | Set | 112933 | 5277
23.11 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 33/0.433KV Delta-Star Connected, Vector Group Dyn 11, ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-1, including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve(above 800 Kva) Suitable size HT cable box, LT cable box or Busduct adaptor box, Off -LTC (+/- 2.5%, +/- 5% to - 7.5% ), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, Unidirectional rollers for rating upto 800 kva & bi- directionalabove 800 Kva rollers with locking arrangement etc. as required. The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM's own lab shall be witnessed by Department engineer Physically. Transformer shall be tested from CTL of discom before charging of transformer & complete installaion must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)Following tests shall be carried out on each transformer at site by OEM enginer in presence of department authorised representative:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test.
Note :Manufacturer testing labotatory to be NABL certified with in house core cutting facility for proper control & monitoring of quality & to avoid mixing of Prime core with Second grade /defective core materials, The core shall be constructed from high grade, non ageing, PRIME GRADE CRGO with M4 Grade or Better, silicon steel laminations and shall be of boltness design. The core and coil assembly should be dried through a highly efficient vacuum drying autoclave for heating and drying.
23.11.1 | 1000 KVA with % Impedance 5.0 | Set | 1988134 | 33330
23.11.2 | 1250 KVA with % Impedance 5.0 | Set | 2560299 | 38885
23.11.3 | 1600 KVA with % Impedance 6.25 | Set | 2792498 | 44440
23.11.4 | 2000 KVA with % Impedance 6.25 | Set | 3251341 | 49995
23.11.5 | 2500 KVA with % Impedance 6.25 | Set | 3653523 | 55550
23.12 | Add Extra for On load tap changer (OLTC) (+5% to - 15% @ 1.25%) and Remote tap changer control (RTCC) panel with Automatic voltage regulator (AVR) in place of Off circuit tap chaner (OCTC) for 33/0.433 KV Transformer | Set | 543834 | 5555
23.13 | Supply, installation, testing & commissioning of Outdoor (IP55) 33kV 630Amps STC 25KA/3 sec. Non Extensible/Extensible Ring Main Unit Compact switchgear consisting of fixed motorized load break switch with earth switch module & fixed Motorized Vacuum Circuit Breaker Module with 25KA for 3 Sec breaking capacity (with Offload isolator & earth switch) and copper Busbar in SF6 insulated stainless steel enclosure (2 mm thick, SS304 grade). Minimum 3 modules to be accommodated in one gas tank to avoid multiple coupling. The complete RMU must be type tested for Internal arc 25KA for 1 sec with AFLR Classification for Gas tank & Cable Chamber. HT RMU shall preferably have site replaceable bushings to have very less downtime in the event of bushing breakage and restoration can be done immediately without sending the RMU to OEM Works. The Vaccum Interrupter must be RMU manufacturer's own make. Channel partner / System Integrator / Authourized Partner/ License partner make RMU shall not be accepted. Microprocessor based IDMT Relay for Circuit Breakers - Self Powered along with series trip coil (Modbus RS485 complaint) for each VCB Module. Capacitive voltage indication fixed type system with LED for all feeder cable bushing & SF6 Gas pressure indicator on the gas tank & Fault passage indicator for each LBS module to be provided. Operating sequence of VCB must be O-0.3Sec-CO-15 Sec-CO or as per type test and suitable for 10000 CO mechanical operation. CT shall be minimum 40/1A ,2.5VA , 5P20 - 3 nos. for protection. Touch proof screen separable right angle boot to be provided in each module as RMU OEM's recommended make and termination to be done by RMU OEM at site. 12VX2, 26AH Battery & 7A Charger to be provided along with RMU. 230A AC input supply shall be extended at site by the client.
23.13.1 | Extensible 3 Way RMU consisting of 2 LBS & 1 VCB | Set | 2584542 | 16665
23.13.2 | Non-Extensible 3 Way RMU consisting of 2 LBS & 1 VCB | Set | 2526181 | 16665
23.13.3 | Non-Extensible 4 Way RMU consisting of 2 LBS & 2 VCB | Set | 3733688 | 27775
23.13.4 | Non-Extensible 1 Way RMU consisting of 1 VCB & One Side cable entry | Set | 1221957 | 13888
23.13.5 | Metering Module having PT and MFM in Each VCB Moudle | Set | 364025 | 13888
23.13.6 | Touch Proof termination kit for Above RMU upto 300 Sq.mm along with Jointing at site | Set | 95599 | 2222
23.14 | Supply & Installation of D.P. Structure With AIR BREAK SWITCH having following specifications A, B, C, D, E. All as per pre approved by Engineer in charge.
A) Double pole structure on 2 no ISMB ( I beam ) of size 150 x 75 mm, 10 mtr length using 7 no MS channel each of size 100 mm x 50 mm x 2500 mm complete in all respect with nuts, springs washers, clamps as required.
B) Off load type gang operated 3-pole vertical flute type switch suitable for 33KV ; 800A ,3-ø, central post rotating double break isolator without EB with 18*24KV Post, complete with MS hardware , copper moving & fixed contact,GI pipe of suitable length for operation.
C) 3nos Vertical / Horizontal mounted 33kv horn gap fuse set of 12*24 KV post insulators
D) 3 piece non linear resistor type. lighting arrestor of approved make suitable for 3 wire, 33kv Overhead line with rated voltage of 30kv rms & nominal discharge current rating of 10 ka & complete with galvanized clamping arrangement GI bolts, nuts, washer etc as required.
| E) 3 no 33kv ACSR conductors mounted on pin type insularors as required. 6.GENERAL:The go shall be operated by hand operated liver properly earthed with provision for locking mounted at 3’ | Set | 152165 | 22220
23.15 | Supplying, Installation, Testing & Commissioning indoor type VCB Panel (Panel Fabricated in VCB Manufacturer's own Factory) shall be Standard made from pre-fabricated, High quality Aluminium-Zinc (Aluzinc) coated sheet steel or CRCA sheet for Construction of Panel for better corrosion resistance. Doors and End Covers would be of Powder Painted CRCA Sheet of 2 mm thickness. Floor mounted metal enclosed, 33 KV VCB panel with totally enclosed and fully interlocked, horizontal draw out, horizontal isolation type breaker as per IEC-62271-1,100,200, as amended up to date and additional SPecifications, having capacities as mentioned below, single break, trip free mechanism, manually charged and manually closing breaker suitable for use on 33 KV, 3 phase, 50 Hz A.C. supply with short circuit fault level of 26 kA for 3 sec , Panel shall be full internal arc tested i.e. in all three chambers at 26 kA for 1 sec for safety purpose (AFLR). compete with self contained, fully interlocked, rack in and rack out mechanism, air insulated HT sleeved (PVC sleeve is not accepted) self supported Aluminium bus bars of 630 current capacity, breaker featured with mechanical ON/ OFF indicator with hand trip coil and auxiliary switch of 4 NO+4NC and equipped with following switchgears and accessories. Make of Vacuum interrupter, circuit breaker, Panel, relays & meters shall be same. VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. Cable compartment suitable for 2RX3C x 240 sq. mm XLPE 33 KV cable (Cable entry from bottom) end termination with heat shrinkable jointing material etc as reqd. There must be a viewing window on VCB chamber door and same must be as per Internal arc test report. The basic insulation level of entire panel shall be 70KV(RMS) / 170KV(Peak).
23.15.1 | Incoming cum Outgoing 630 Amp VCB Panel with Additional Cable Box at Back side for Cable Termination
a) 630 Amp VCB - 1 Nos
b) 33 KV / 110 Volts PT Class 0.5 accuracy and 50 VA burden with 1 No. Voltmeter(0-15 KV), digital type selector switch for voltmeter and protection fuses / MCB for HT metering upto 12 KV on incomer. (0-50-100A) comply with IS 3156. PT must not be on the top of the panel. It must be floor rooled placed rear side of panel or on the CB trolley -1 Set.
c) Digital type multi function meter and Digital type Ammeter & Voltmeter - 1 No.
d) Flush mounted type Microprocessor based numercial IDMT relay (VCB Panel manufacturer's own Make) with O/L, E/L and S/C communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs. -1 No.
e) Dual core /single core;separate sets, dual ratio 3 Nos. CTs 200/100/1 A of 5 VA burden and accuracy class 0.5 for metering and class 5P10 for protection comply with IS 2705 - 1 Set
f) R,Y,B ON, OFF, Trip Indication with Control MCB - 1 Set
g) Annunciator -8 Window- 1Set
h) Flash mounted Aux. Relay as required for OTI, WTI & Buchloz Alarm & Trip functions
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 1098890 | 31397
23.15.2 | Incoming - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) 33 KV / 110 Volts PT Class 0.5 accuracy and 50 VA burden with 1 No. Voltmeter(0-15 KV), digital type selector switch for voltmeter and protection fuses / MCB for HT metering upto 12 KV on incomer. (0-50-100A) comply with IS 3156. PT must not be on the top of the panel. It must be floor rooled placed rear side of panel or on the CB trolley -1 Set.
c) Digital type multi function meter and Digital type Ammeter & Voltmeter - 1 No.
d) Flush mounted type Microprocessor based numercial IDMT relay (VCB Panel manufacturer's own Make) with O/L, E/L and S/C communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs. -1 No.
e) Dual core /single core;separate sets, dual ratio 3 Nos. CTs 200/100/1 A of 5 VA burden and accuracy class 0.5 for metering and class 5P10 for protection comply with IS 2705 - 1 Set
f) R,Y,B ON, OFF, Trip Indication with Control MCB - 1 Set
g) Annunciator -8 Window- 1Set
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 944906 | 26997
23.15.3 | Outgoing - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) Digital type multi function meter & Digital ammeter-1 Nos.
c) Flush mounted type Microprocessor based numercial IDMT relay with O/L, E/L and S/C, Arc fault protection communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs- 1 Nos.
d) Dual core dual ratio 3 CTs 100/50/1 A of 5 VA burden and accuracy Class-0.5 for metering and class 5P10 for protection - 3 Nos.
e) Annunciator -8 Window- 1 Nos
f) Hooter - 1 Nos
g) Flash mounted Aux. Relay as required for OTI, WTI & Buchloz Alarm & Trip functions
h)Trip super vision Relay - 1 Nos.
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 909909 | 25997
23.15.4 | Buscoupler with Riser - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) Digital type multi function meter & Digital ammeter-1 Nos.
c) Dual core dual ratio 3 CTs 100/50/1 A of 5 VA burden and accuracy Class-0.5 for metering and class 5P10 for protection - 3 Nos.
d) Annunciator -8 Window- 1 Nos
e) Hooter - 1 Nos
| f)Trip super vision Relay - 1 Nos. | Each | 839916 | 23998
23.16 | Supplying, Installation, Testing & Commissioning indoor type VCB Panel (Panel Fabricated by System Integrator of VCB Manufacturer) shall be Standard made from pre-fabricated, Construction of Panel, Doors and End Covers would be of Powder Painted CRCA Sheet of 2 mm thickness. Floor mounted metal enclosed, 33 KV VCB panel with totally enclosed and fully interlocked, horizontal draw out, horizontal isolation type breaker as per IEC-62271-1,100,200, as amended up to date and additional SPecifications, having capacities as mentioned below, single break, trip free mechanism, manually charged and manually closing breaker suitable for use on 33 KV, 3 phase, 50 Hz A.C. supply with short circuit fault level of 26 kA for 3 sec. compete with self contained, fully interlocked, rack in and rack out mechanism, air insulated HT sleeved (PVC sleeve is not accepted) self supported Aluminium bus bars of 630 current capacity, breaker featured with mechanical ON/ OFF indicator with hand trip coil and auxiliary switch of 4 NO+4NC and equipped with following switchgears and accessories. Make of Vacuum interrupter, circuit breaker, Panel, relays & meters shall be same. VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. Cable compartment suitable for 2RX3C x 240 sq. mm XLPE 33 KV cable (Cable entry from bottom) end termination with heat shrinkable jointing material etc as reqd. The basic insulation level of entire panel shall be 70KV(RMS) / 170KV(Peak).
23.16.1 | Incoming cum Outgoing 630 Amp VCB Panel with Additional Cable Box at Back side for Cable Termination
a) 630 Amp VCB - 1 Nos
b) 33 KV / 110 Volts PT Class 0.5 accuracy and 50 VA burden with 1 No. Voltmeter(0-15 KV), digital type selector switch for voltmeter and protection fuses / MCB for HT metering upto 12 KV on incomer. (0-50-100A) comply with IS 3156. PT must not be on the top of the panel. It must be floor rooled placed rear side of panel or on the CB trolley -1 Set.
c) Digital type multi function meter and Digital type Ammeter & Voltmeter - 1 No.
d) Flush mounted type Microprocessor based numercial IDMT relay (VCB Panel manufacturer's own Make) with O/L, E/L and S/C communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs. -1 No.
e) Dual core /single core;separate sets, dual ratio 3 Nos. CTs 200/100/1 A of 5 VA burden and accuracy class 0.5 for metering and class 5P10 for protection comply with IS 2705 - 1 Set
f) R,Y,B ON, OFF, Trip Indication with Control MCB - 1 Set
g) Annunciator -8 Window- 1Set
h) Flash mounted Aux. Relay as required for OTI, WTI & Buchloz Alarm & Trip functions
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 915742 | 26164
23.16.2 | Incoming - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) 33 KV / 110 Volts PT Class 0.5 accuracy and 50 VA burden with 1 No. Voltmeter(0-15 KV), digital type selector switch for voltmeter and protection fuses / MCB for HT metering upto 12 KV on incomer. (0-50-100A) comply with IS 3156. PT must not be on the top of the panel. It must be floor rooled placed rear side of panel or on the CB trolley -1 Set.
c) Digital type multi function meter and Digital type Ammeter & Voltmeter - 1 No.
d) Flush mounted type Microprocessor based numercial IDMT relay (VCB Panel manufacturer's own Make) with O/L, E/L and S/C communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs. -1 No.
e) Dual core /single core;separate sets, dual ratio 3 Nos. CTs 200/100/1 A of 5 VA burden and accuracy class 0.5 for metering and class 5P10 for protection comply with IS 2705 - 1 Set
f) R,Y,B ON, OFF, Trip Indication with Control MCB - 1 Set
g) Annunciator -8 Window- 1Set
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 787421 | 22498
23.16.3 | Outgoing - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) Digital type multi function meter & Digital ammeter-1 Nos.
c) Flush mounted type Microprocessor based numercial IDMT relay with O/L, E/L and S/C, Arc fault protection communicable on modbus protocal for protection and Status monitoring with Master trip and Trip Ckt Supervision relay. Relay shall have programable 4 digital Inputs and 6 outputs- 1 Nos.
d) Dual core dual ratio 3 CTs 100/50/1 A of 5 VA burden and accuracy Class-0.5 for metering and class 5P10 for protection - 3 Nos.
e) Annunciator -8 Window- 1 Nos
f) Hooter - 1 Nos
g) Flash mounted Aux. Relay as required for OTI, WTI & Buchloz Alarm & Trip functions
h)Trip super vision Relay - 1 Nos.
| i) Power panel pack with 220 Volt AC input & 110V Volt DC continuous output suitable for closing / tripping / indication etc | Each | 758258 | 21665
23.16.4 | Buscoupler with Riser - 630 Amp VCB and each shall be consisting of
a) 630 Amp VCB - 1 Nos
b) Digital type multi function meter & Digital ammeter-1 Nos.
c) Dual core dual ratio 3 CTs 100/50/1 A of 5 VA burden and accuracy Class-0.5 for metering and class 5P10 for protection - 3 Nos.
d) Annunciator -8 Window- 1 Nos
e) Hooter - 1 Nos
| f)Trip super vision Relay - 1 Nos. | Each | 699930 | 19998
23.17 | SITC of following capacity IK10 Sandwich Type Rising Mains / Bus Bar trunking Confirming to IEC 61439 part 1 & part 6 standard & IS 8623 P-II and Manufactured in India for use on 3 phase 4 wire , 50% integral earth , 415 volts, 50Hz A.C. supply , class F insulation, rated insulation voltage 1000V, impulse withstand voltage 12 KV, min. seismic zone 5 as per IS1893 (Part 1) , with IP-54/ IP-55 / IP-65(with Canopy) enclosure made of 1.5 mm thick sheet steel duly powder coated in convenient sections complete with 4 Nos aluminium (with IS 19501 or superior) bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre,continuous external earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system including making opening in RCC / Brick Masonary and repairing the same etc. as required. Type Tests reports like (i) Short Circuit Test (ii) Degree of Protection (iii) Temperature rise test of Rising main in CPRI / UL / ASTA/ LOVAG accrediated lab will be submitted by OEM.
Note : Routine tests, as per OEM's QAP shall be conducted at the manufacturers facility in India and witnessed by the Departmental Engineer, either virtually or physically. Furthermore, complete Installation of Rising Mains shall be Vetted by Manufacturer before Comissioning.
23.17.1 | Sandwich Type Bus Rising Main IP-54
23.17.1.1 | 400 amps 25 KA SC for 1 sec | Mtr | 15380 | 1053
23.17.1.2 | 630 amps 40 KA SC for 1 sec | Mtr | 18047 | 1236
23.17.1.3 | 800 amps 50 KA SC for 1 sec | Mtr | 20794 | 1424
23.17.1.4 | 1000 amps 50 KA SC for 1 sec | Mtr | 22886 | 1568
23.17.1.5 | 1250 amps 50 KA SC for 1 sec | Mtr | 25633 | 1756
23.17.1.6 | 1600 amps 50 KA SC for 1 sec | Mtr | 29301 | 2007
23.17.1.7 | 2000 amps 65 KA SC for 1 sec | Mtr | 36356 | 2490
23.17.2 | Sandwich Type Bus Duct IP-55
23.17.2.1 | 1000 Amps 50kA SC for 1 sec | Mtr | 25306 | 1733
23.17.2.2 | 1250 Amps 65kA SC for 1 sec | Mtr | 29157 | 1997
23.17.2.3 | 1600 Amps 80kA SC for 1 sec | Mtr | 34153 | 2339
23.17.2.4 | 2000 Amps 80kA SC for 1 sec | Mtr | 42196 | 2890
23.17.2.5 | 2500 Amps 80 kA SC for 1 sec | Mtr | 53436 | 3660
23.17.2.6 | 3200 Amps 100kA SC for 1 sec | Mtr | 66141 | 4530
23.17.2.7 | 4000 Amps 100kA SC for 1 sec | Mtr | 76819 | 5262
23.17.2.8 | 5000 Amps 100kA SC for 1 sec | Mtr | 94900 | 6500
23.17.3 | Out Door Bus Duct IP65 with External Canopy
23.17.3.1 | 1000 Amps 50kA SC for 1 sec | Mtr | 28006 | 1918
23.17.3.2 | 1250 Amps 65kA SC for 1 sec | Mtr | 32466 | 2224
23.17.3.3 | 1600 Amps 80kA SC for 1 sec | Mtr | 38665 | 2648
23.17.3.4 | 2000 Amps 80kA SC for 1 sec | Mtr | 48074 | 3293
23.17.3.5 | 2500 Amps 80 kA SC for 1 sec | Mtr | 55836 | 3824
23.17.3.6 | 3200 Amps 100kA SC for 1 sec | Mtr | 71438 | 4893
23.17.3.7 | 4000 Amps 100kA SC for 1 sec | Mtr | 86405 | 5918
23.17.3.8 | 5000 Amps 100kA SC for 1 sec | Mtr | 105565 | 7230
23.18 | SITC of Bus Rising Main OEM manufactured following capacity End Feed Unit Confirming to ANSI C37.23 standard & IS 8623 P-II suitable for Sandwich / Compact Air Insulated type for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.5 mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB), Interlocking feature complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required. .
23.18.1 | For 200 Amp. (Without MCCB) | Each | 10465 | 717
23.18.2 | For 250 Amp. (Without MCCB) | Each | 11639 | 797
23.18.3 | For 325 Amp. (Without MCCB) | Each | 12816 | 878
23.18.4 | For 400 Amp. (Without MCCB) | Each | 16347 | 1120
23.18.5 | For 500 Amp. (Without MCCB) | Each | 17263 | 1182
23.18.6 | For 630 Amp. (Without MCCB) | Each | 19878 | 1362
23.18.7 | For 800 Amp. (Without MCCB) | Each | 28117 | 1926
23.18.8 | For 1000/1250 Amp. (Without ACB) | Each | 91545 | 6270
23.18.9 | For 1600 Amp. (Without ACB) | Each | 10585 | 7300
23.18.10 | For 2000 Amp. (Without ACB) | Each | 130256 | 8920
23.19 | SITC of following capacity IK10 Compact Air Insulated Rising Mains / Bus Bar trunking Confirming to IEC 61439 part 1 & part 6 standard & IS 8623 P-II and Manufactured in India for use on 3 phase 4 wire , 50% integral earth from enclosure , 415 volts, 50Hz A.C. supply , The busbars shall be supported through class “F” Insulator at interval not exceeding 250mm. impulse withstand voltage 12 KV, min. seismic zone 4 as per IS1892, with IP-54 enclosure made of 1.5 mm thick sheet steel duly powder coated in convenient sections complete with 4 Nos aluminium (with 6101 or 63401 grade) bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system including making opening in RCC / Brick Masonary and repairing the same etc. as required.
Type Tests reports like (i) Short Circuit Test (ii) Degree of Protection (iii) Temperature rise test of Rising main in CPRI / UL / ASTA/ LOVAG accrediated lab will be submitted by OEM.
Note : Routine tests, as per OEM's QAP shall be conducted at the manufacturers facility in India and witnessed by the Departmental Engineer, either virtually or physically. Furthermore, complete Installation of Rising Mains shall be Vetted by Manufacturer before Comissioning.
23.19.1 | 200 amps 10 KA SC for 1 sec | Mtr | 9547 | 654
23.19.2 | 250 amps 15 KA SC for 1 sec | Mtr | 1005 | 685
23.19.3 | 315 amps 25 KA SC for 1 sec | Mtr | 10920 | 748
23.19.4 | 400 amps 30 KA SC for 1 sec | Mtr | 12058 | 826
23.19.5 | 500 amps 35 KA SC for 1 sec | Mtr | 13732 | 941
23.19.6 | 630 amps 50 KA SC for 1 sec | Mtr | 16282 | 11115
23.19.7 | 800 amps 50 KA SC for 1 sec | Mtr | 20898 | 1431
23.19.8 | 1000 amps 50 KA SC for 1 sec | Mtr | 23344 | 1599
23.20. | SITC of Bus Rising Main OEM manufactured following capacity Plug in / Tap off Box suitable for Sandwich / Compact Air Insulated type bus bar trunking Confirming to ANSI C37.23 standard & IS 8623 P-II & IEC-60947-2-2000 for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCB/MCCB / ACB (but without MCB/MCCB/ACB) with Interlocking complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
23.20.1 | Plug in Box suitable for Sandwich Type Bus rising Main
23.20.1.1 | up to 63 amps FP (Suitable for MCB) without MCB Without Interlocking | Each | 6840 | 469
23.20.1.2 | 63 amps (Suitable for MCCB) without MCCB | Each | 8017 | 549
23.20.1.3 | 100/125 amps (Suitable for MCCB) without MCCB | Each | 8671 | 594
23.20.1.4 | 160/200/250 amps (Suitable for MCCB) without MCCB | Each | 11410 | 782
23.20.1.5 | 400 amps (Suitable for MCCB) without MCCB | Each | 13483 | 924
23.20.1.6 | 500 / 630 amps (Suitable for MCCB) without MCCB | Each | 18891 | 1294
23.20.2 | Plug in Box suitable for Compact Air Insulated Type Bus rising Main
23.20.2.1 | up to 32 amps (Suitable for MCB) without MCB Without Interlocking | Each | 5689 | 390
23.20.2.2 | 63 amps (Suitable for MCCB) without MCCB | Each | 7193 | 493
23.20.2.3 | 100/125 amps (Suitable for MCCB) without MCCB | Each | 7454 | 511
23.20.2.4 | 160/200/250 amps (Suitable for MCCB) without MCCB | Each | 9155 | 627
23.20.2.5 | 400 amps (Suitable for MCCB) without MCCB | Each | 119001 | 815
23.20.2.6 | 630 amps (Suitable for MCCB) without MCCB | Each | 15824 | 1084
23.21 | SITC of OEM's manufactured Bus Rising Main having Tinned copper flexible joint with enclosure of following capacity with Transformer / DG / Panel as required complete in all respect.
23.21.1 | 1000 Amp. Rating | Each | 40541 | 2777
23.21.2 | 1250 Amp. | Each | 58850 | 4031
23.21.3 | 1600 Amp. | Each | 71928 | 4927
23.21.4 | 2000 Amp. | Each | 112470 | 7703
23.21.5 | 2500 Amp. | Each | 138625 | 9495
23.21.6 | 3200 Amp. | Each | 17393 | 11913
23.21.7 | 4000 Amp. | Each | 227555 | 15586
23.21.8 | 5000 Amp. | Each | 282482 | 19348
23.22 | SITC of following capacity bus trunking with aluminium bus bars, The busbars shall be supported through class “F” Insulator, Enclosure made of 1.6mm thick sheet steel duly powder coated in convenient sections for use on, 3 phase, 4 wire,415 V, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
23.22.1 | 800 Amp. | Mtr | 11666 | 799
23.22.2 | 1000 Amp. | Mtr | 14255 | 976
23.22.3 | 1250 Amp. | Mtr | 16740 | 1147
23.22.4 | 1600 Amp. | Mtr | 20271 | 1388
23.22.5 | 2000 Amp. | Mtr | 24586 | 1684
23.23 | SITC of HT metering cubical panel (as approved By DISCOMs) fabricated from 20 SWG CRCA sheet steel having two compartments & MS angle of size 60mmX 6mm. It should have provision for Following: (i) fixing Trivector / Import - Export Meter (To be supplied by DISCOMs) (ii) fixing of combined CT PT Set with Copper strip for Connection (To be supplied by DISCOMs), (iii)Test terminal Block, (iv) 6mm thick Bakelite sheet on all sides, (V) 3/6 corex 1.5 / 2.5 Sq.mm copper cable for interconnections, etc. as required. . | Set | 29425 | 2015
23.24 | SITC of Radiator Cooled Silent DG Set (As per latest CPCB-IV+ emission norms) having specifications as per A, B, C, D, E, F & G :
A) Diesel Engine : Turbo charged Diesel Engine ( conforming to BS:649/5514), multi cylinder, dynamically balanced flywheel, electric start of suitable BHP at 1500 rpm capable of taking 10% over loading for one hour after 12 hours of continuous operation., Dry exhaust mainfold with silencer and Diesel oxidation catalyst & selective catalyst reduction system (isolated from main DG chamber), up to 1.50 M exhaust piping (with LRB insulation & Alum. cladding ) as required .Diesel engine should have Precise emission control by treatment with Diesel exhaust fluid (DEF)/Aqueous urea tank (above 82.5 KVA) as per CPCB 4+ norms
B) Alternator : AC Brush less SPDP Synchronous alternator rated of appropriate KVA, 415 volts at 1500 rpm, 3 phase, 50 Hz, ac supply with 0.8 lagging power factor. Alternator conforming to BS 5000 (part 99) or IS/IEC 60034-1. . Alternator shall be self regulated with standard Alternator Protection( Over voltage , over speed & under voltage, under speed warning & shutdown).
C) Canopy : CPCB / ARAI approved Standard canopy with Weatherproof, powder coated Accoustic enclosure for DG set for sound attenuation fabricated from CRCA sheet steel (structure) including sidewals & filled with glasswool (96Kg/m3) /PU Foam. as per IS8183 and the thickness of the doors should be 28/40/50/85 mm as per rating . All doors/opening are sealed with neoprene /EPDN gaskets. The DG Set has Inbuilt / External in fuel tank to run 6 to 8 Hrs along with DEF tank (as per OEM standards). There should be provision of protection and tripping of DG set for temperature greater than 50 degree centigrade. The enclosure should be suitable for following capacity DG sets and alternator. Noise level shall be less than 75 dB at a distance of 1 Mtrs. in open free field environment as per ISO 8528 part 10 duly certified by authorised agency etc.
D) Instruments : Electronic / Mechanical governor, Manual & electric Start ,Batteries with battery charger, Electronic fuel system, advanced after treatment system (ATS), Exhaust gas recirculation(EGR) System along with Diesel oxidation catalyst(DOC) and Selective catalytic reduction (SCR) , supply module and DCU to control and monitor DEF. Engine instruments panel should have microprocessor based Genset monitoring system capable of displaying Running Hour, RPM, lubbrication oil pressure indication, lubrication oil temperature, battery charging indication, overspeed indication, fuel level etc. The control Panel should equipped with MCCB/ACB of suitable rating.
E) Base frame and foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel & coupled through a flexible coupling or close coupled which shall be installed on existing cement concrete foundation and vibration isolation arrangements as per recommendation of manufacturer.
F) First filling of the FUEL Tank and DEF tank shall be done by contractor.
G) DG set will be offered for Inspection and Testing at OEM's Works ( as per approved QAP ) in presence of Departmental Engineers .In case of 13 hour running testing at OEM's works, cost of actual consumables will be reimbursed.
Note: 1. During the DLP, the contractor shall arrange for servicing of the DG set through authorized dealer of OEM, as per the manufacturers guidelines. The actual cost of consumables used during servicing will be reimbursed to the contractor by the end user department. 2. Manufacturer / OEM must have its authorized service dealer in Rajasthan. Which can provide service within 6 Hours of compalint registration.
23.24.1 | 20 KVA at 0.8 pf 415V 50Hz 3-ǿ with 2 Cylinder Engine | Set | 441817 | 10570
23.24.2 | 25 KVA at 0.8 pf 415V 50Hz 3-ǿ with 2 Cylinder Engine | Set | 553156 | 13233
23.24.3 | 30 KVA at 0.8 pf 415V 50Hz 3-ǿ with 2 Cylinder Engine | Set | 568342 | 13597
23.24.4 | 40 KVA at 0.8 pf 415V 50Hz 3-ǿ with 2 Cylinder Engine | Set | 615432 | 14723
23.24.5 | 50 KVA at 0.8 pf 415V 50Hz 3-ǿ with 2 Cylinder Engine | Set | 686189 | 16415.9971
23.24.6 | 58.5 KVA at 0.8 pf 415V 50Hz 3-ǿ with 4 Cylinder Engine | Set | 718795 | 17196
23.24.7 | 82.5 KVA at 0.8 pf 415V 50Hz 3-ǿ with 4 Cylinder Engine | Set | 969802 | 23201
23.24.8 | 100 KVA at 0.8 pf 415V 50Hz 3-ǿ with 4 Cylinder Engine | Set | 1139819 | 27268
23.24.9 | 125 KVA at 0.8 pf 415V 50Hz 3-ǿ with 4 Cylinder Engine | Set | 1179420 | 28216
23.24.10 | 140 KVA at 0.8 pf 415V 50Hz 3-ǿ with 4 Cylinder Engine | Set | 1307129 | 31271
23.24.11 | 160 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 1512440 | 36183
23.24.12 | 180 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 1587161 | 37970
23.24.13 | 200 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 1653106 | 39548
23.24.14 | 250 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 2053974 | 49138
23.24.15 | 320 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 2592003 | 62010
23.24.16 | 400 KVA at 0.8 pf 415V 50Hz 3-ǿ with 6 Cylinder Engine | Set | 3504951 | 83851
23.24.17 | 500 KVA at 0.8 pf 415V 50Hz 3-ǿ with 8 Cylinder Engine | Set | 3921145 | 93807
23.24.18 | 625 KVA at 0.8 pf 415V 50Hz 3-ǿ with 10 Cylinder Engine | Set | 5874921 | 112979
23.24.19 | 750 KVA at 0.8 pf 415V 50Hz 3-ǿ with 12 Cylinder Engine | Set | 6458881 | 124209
23.25 | Providing, Fixing, Jointing, Testing & Commissioning of Medium duty MS B class pipes conforming to IS 3589 / 1239 part-I for DG Exhaust applications (beyond 1.5 Mtr. length) including cutting, welding etc & fittings like elbows,flanges, tapers, reducer, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, hanger and nuts bolts . including the cost of thermal insulation with 50 mm thick layers of LRB rock wool as per IS : 8183-1993 (64 kg/m3 density) & 26 SWG aluminium sheet claddings etc complete as required complete in all respect. (Cost of Steel Structure for Exhaust pipe will be paid Extra). .
23.25.1 | 80 mm dia | Mtr | 2869 | 733
23.25.2 | 100 mm dia | Mtr | 3661 | 935
23.25.3 | 125 mm dia | Mtr | 4571 | 1168
23.25.4 | 150 mm dia | Mtr | 5687 | 1453
23.25.5 | 200 mm dia | Mtr | 8277 | 2115
23.25.6 | 250 mm Dia. | Mtr | 11021 | 2816
23.26 | Supply, installation and testing of metal flexible coupling (bellow) of following dia required for horizontal length more than 3 mtr.as per standard of guide line of D.G. set company complete in all respect. .
23.26.1 | 80 mm dia | Each | 11889 | 1062
23.26.2 | 100 mm dia | Each | 13781 | 1230
23.26.3 | 125 mm dia | Each | 15672 | 1399
23.26.4 | 150 mm dia | Each | 19636 | 1753
23.26.5 | 200 mm dia | Each | 22474 | 2007
23.26.6 | 250 mm Dia. | Each | 30085 | 2686
23.27 | SITC of Auto main failure (AMF) Panel fabricated from CRCA sheet steel 2 mm Thick , Powder coated finish , Engine Start & Stop commands, control Relays , Ammeter & Voltmeter with selector switches, Control & 2 nos of required size 4 pole AC1 duty Power Contactors with 2 no. of required size 4 pole MCCB with Icu=100% Ics 25KA breaking capacity upto 200KVA & 50 KA above 200 KVA rating with adjustable O/L & fixed Short circuit, Timers, Electronic Hooter ,Visual & Alarm indication for faults, UPS, operator interface panel complete in all respect suitable for following capacity DG sets: ( M S / RCC structure required for AMF panel will be paid extra )
23.27.1 | 20 to 40 KVA | Each | 71000 | 5555
23.27.2 | 50 to 82.5 KVA | Each | 84087 | 5555
23.27.3 | 100 to 140 KVA | Each | 100746 | 5555
23.27.4 | 160 to 200 KVA | Each | 139219 | 8333
23.27.5 | 250 KVA | Each | 174916 | 8333
23.27.6 | 320 KVA | Each | 198714 | 8333
23.27.7 | 380 KVA | Each | 219339 | 11110
23.27.8 | 500 KVA | Each | 278833 | 11110
23.28 | Supply & fabrication steel structure with MS channel / angle / joist / ISMB / sheet etc. including welding, rivetting, cutting, nut & bolt , one coat of primer & two coat of enamel paint etc. as required complete in all respect. . | Kg | 114 | 18
23.29 | Earth work in excavation/ by mechanical means (Hydraulic Excavator) / Manual means over areas (exceeding 30 cm in depth, 1.5m in width as well as 10 sum on plan) including disposal of excavated earth, lead upto 50 m and lift upto 1.5 m, disposed earth to be levelled and neatly dressed: | cum | 178 | 178
23.30. | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with Cement Mortar 1:6 ( 1-Cement : 6-Sand). | cum | 5855 | 1889
23.31 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. | Kg | 87 | 13
23.32 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level
23.32.1 | 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | cum | 4381 | 1889
23.32.2 | 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) | cum | 4155 | 1889
23.32.3 | 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | cum | 3928 | 1889
23.33 | Plaster on new surface on wall in cement sand mortar 1:4 including racking of joints etc. complete fine finish :
23.33.1 | 20mm thick | Sqm | 404 | 178
23.33.2 | 12mm thick | Sqm | 325 | 178
23.34 | Finishing wall with water proofing cement paint of approved brand and manufacture and or required shade to give an even shade including all scaffolding:
23.34.1 | New work (Two or more coats applied @ 3.84 kg/10 sqm). | Sqm | 140 | 61
23.35 | Providing and fixing welded mesh/expanded metal mesh 25 mmx 25 mm x 3mm in frame work, flat iron beading 20x3mm including top cross laps inside and out sides welding, iron bolts, crews, clips etc. including two coat of red oxide and two coat of enamel paint or more required complete with frame work with 50 X 50 X 6mm angle iron post 30 cm in ground embeded in cement concrete 1:3:6 (30X30X45cm) at corner and every three mtr including painting with one coat of primer and two coat of enamel paint work will be done as per direction of engineer incharge of size complete in all respect. . | Sqm | 1580 | 337
23.36 | Gravelling of Transformer / RMU Yard with 100 mm Height Gravels of Size 20 to 25 mm including leveling, Dressing etc. as Required. | Sqm | 1127 | 333

## ch 24 Fire Protection Work
Chapter E - 24
Fire Protection Work
S.No. | Description | Unit | Complete Rate without GST | ITC rate without GST
24.1 | Supplying, Installation, Testing & Commissioning of Electrical Driven fire fighting duty pump as per TAC and IS 12469-1988., Factory assembled in Pump make OEM for Sprinkler / Hydrant applications suitable for automatic operation and consisting of following details given as A, B, C, D, E, F, G and H.
(A) End Suction / Horizontal Axially split casing volute type Single / Multi stage Centrifugal pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pump Casing - PN-16,Cast Iron, Impellor - Bronze/SS-304, Shaft - SS 410, Packing - Mechanical Seal
(C)Pump shall be capable of delivering not less than 150 % of rated capacity at a head not less than 65 % of the rated head. The shut off head shall not exceed 120 % of rated head
(D) Squirrel cage induction motor (IE-3 Class) suitable for 3 phase, 415 V, 50 HZ, Ac supply , Class -F Insulation, Synchronous speed 2900 / 1500 RPM, T.E.F.C confirming to IP:55 , of required HP suitable for the above pump ,along with flexible (LoveJoy type) coupling , coupling guard complete in all respect .
( E) Common bed plate fabricated from mild steel channel for installation of pump and Motor including anti vibration pads.
(F) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Physical presence of Department’s representatives. or by Third Party like RITES / PDIL / EIL
(G) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted by OEM
(H) Pumpset to be placed on Suitable size Reinforced cement concrete (M-30) foundation with foundation bolt, Nozing Angle of size 40mm x 40mm x 5 mm ( Cost of RCC Foundation to be paid Extra See Chapter -23).
24.1.1 | 1620 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage, 2900 RPM | Each | 248584 | 11616
24.1.2 | 1620 LPM suitable for 70 Mtr Head End Suction Back pull type Single Stage, 2900 RPM | Each | 258788 | 12093
24.1.3 | 1620 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 633400 | 29598
24.1.4 | 2280 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage, 2900 RPM | Each | 341889 | 15976
24.1.5 | 2280 LPM suitable for 70 Mtr Head End Suction Back pull type Single Stage, 2900 RPM | Each | 357603 | 16710
24.1.6 | 2280 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 662958 | 30979
24.1.7 | 2850 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage, 2900 RPM | Each | 366204 | 17112
24.1.8 | 2850 LPM suitable for 70 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 632573 | 29560
24.1.9 | 2850 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 748893 | 34995
24.2 | Supplying, Installation, Testing & Commissioning of Diesel Engine Driven fire fighting duty pump as per TAC and IS 12469-1988., Factory assembled in Pump make OEM for Sprinkler / Hydrant applications suitable for automatic operation and consisting of following details given as A, B, C, D, E, F, G and H.
(A) End Suction / Horizontal Axially split casing volute type Single / Multi stage Centrifugal pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pump Casing - Cast Iron, Impellor - Bronze, Shaft - SS 410, Packing - Mechanical Seal
(C)Pump shall be capable of delivering not less than 150 % of rated capacity at a head not less than 65 % of the rated head. The shut off head shall not exceed 120 % of rated head
(D) Heat Exchanger cooled Diesel Engine as per NFPA 20 developing suitable BHP for the below mentioned discharge at 1500 / 1800 RPM, flexible coupling and coupling guard with the Pump, common bed plate for mounting of the Engine and Pump,Antivibration damping arrangement by cushy foot, Diesel Engine starting Panel for starting of the engine automatically if the Normal electrical supply fails with a unit of battery bank of 12/24v,180 Ah, Lead Acid Battery with Boost / Trickle charger as required for operation of Diesel engine, Exhaust Pipe of suitable diameter upto 10 M length (with LRB insulation & Alum. Cladding), with muffler, Diesel tank of 300 Lts capacity (made out from 2 mm thick MS sheet with filling Cap) with drain cock, Diesel level Indicator, Suitable MS angle iron stand for placing tank, first Filling of Diesel tank.
(E) Diesel Engine Control panel comprising Automatic/Manual selctor switch & 3 attempts starting device, timers and relays as required, push buttons, start/stop in manual mode Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication, Battery charger suitbale for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 0- 20 A DC Ammeter,
(F) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Physical presence of Department’s representatives. or by Third Party like RITES / PDIL / EIL
(G) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted by OEM
(H) Pumpset to be placed on Suitable size Existing Reinforced cement concreat (M-30) foundation with foundation bolt, Nosing Angle of size 40mm x40mm x5 mm ( Cost of RCC Foundation to be paid Extra See Chapter -23)
24.2.1 | 1620 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage 2400 RPM | Each | 5283319 | 24688
24.2.2 | 1620 LPM suitable for 70 Mtr Head End Suction Back pull type Single Stage, 2400 RPM | Each | 579198 | 27065
24.2.3 | 1620 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 731191 | 34168
24.2.4 | 2280 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage, 1800 -2400 RPM | Each | 530061 | 24769
24.2.5 | 2280 LPM suitable for 70 Mtr Head End Suction Back pull type Single Stage, 1800 -2400 RPM | Each | 723492 | 33808
24.2.6 | 2280 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 946038 | 44207
24.2.7 | 2850 LPM suitable for 56 Mtr Head End Suction Back pull type Single Stage, 1800 -2400 RPM | Each | 519974 | 24292
24.2.8 | 2850 LPM suitable for 70 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 698001 | 32617
24.2.9 | 2850 LPM suitable for 88 Mtr Head Horizontal Axially split casing volute type Two stage, 1500 RPM | Each | 968331 | 45249
24.3 | Supplying, Installation, Testing & Commissioning of Electrical Driven fire fighting duty Jockey pump as per TAC and IS 12469-1988., Factory assembled in Pump make OEM suitable for automatic operation and consisting of following details given as A, B, C, D, E,F and G
(A) Horizontal End suction Single / Multi Stage Centrifugal Back pull type pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pump Casing - PN-16,Cast Iron, Impellor - Bronze/SS-304, Shaft - SS 410, Packing - Mechanical Seal
(C) Squirrel cage induction motor (IE-3 Class) suitable for 3 phase, 415 V, 50 HZ, Ac supply , Class -F Insulation, Synchronous speed not Exceeding 2900 RPM, T.E.F.C confirming to IP:55 , of required HP suitable for the above pump ,along with flexible (Lovejoy type) coupling , coupling guard complete in all respect .
(D) Common bed plate fabricated from mild steel channel for installation of pump and Motor including anti vibration pads.
(E) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Physical presence of Department’s representatives. or by Third Party like RITES / PDIL / EIL
(F) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted by OEM
(G) Pumpset to be placed on Suitable size Reinforced cement concrete (M-30) foundation with foundation bolt, Nozing Angle of size 40mm x40mm x5 mm ( Cost of RCC Foundation to be paid Extra see chapter - 23 )
24.3.1 | 180 LPM suitable for 88 Mtr Single Stage | Each | 151067 | 7059
24.3.2 | 180 LPM suitable for 70 Mtr Single Stage | Each | 139619 | 6524
24.3.3 | 180 LPM suitable for 56 Mtr Single Stage | Each | 130292 | 6088
24.4 | Supplying, Installation, Testing & Commissioning of Electrical Driven fire fighting duty Jockey pump as per TAC and IS 12469-1988., Factory assembled in Pump make OEM suitable for automatic operation and consisting of following details given as A, B, C, D, E, F and G
(A) Vertical inline Multi Stage Centrifugal pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pump Casing - SS-304, Impellor - SS-304, Shaft - SS- 410, Packing - Mechanical Seal
(C) Squirrel cage induction motor (IE-3 Class) suitable for 3 phase, 415 V, 50 HZ, Ac supply , Class -F Insulation, Synchronous speed not Exceeding 3000 RPM, T.E.F.C confirming to IP:55 , of required HP suitable for the above pump, complete in all respect .
(D) Common bed plate fabricated from mild steel channel for installation of pump and Motor including anti vibration pads.
(E) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Physical / Virtual presence of Department’s representatives. or by Third Party like RITES / PDIL / EIL
(F) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted from OEM
(G) Pumpset to be placed on Suitable size Reinforced cement concrete (M-30) foundation with foundation bolt, Nozing Angle of size 40mm x40mm x5 mm ( Cost of RCC Foundation to be paid Extra see Chapter - 23 )
24.4.1 | 180 LPM suitable for 88 Mtr Multi Stage | Each | 105575 | 4933
24.4.2 | 180 LPM suitable for 70 Mtr Multi Stage | Each | 95908 | 4482
24.4.3 | 180 LPM suitable for 56 Mtr Multi Stage | Each | 90947 | 9250
24.5 | Supplying, Installation, Testing & Commissioning of Electrical Driven fire fighting duty Terrace pump as per TAC and IS 12469-1988., Factory assembled in Pump make OEM suitable for automatic operation and consisting of following details given as A, B, C, D, E, F, G and H
(A) Horizontal End suction Centrifugal Back pull type pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pump Casing - PN-16,Cast Iron, Impellor - Bronze/SS-304, Shaft - SS 410, Packing - Mechanical Seal
(C) Squirrel cage induction motor (IE-3 Class) suitable for 3 phase, 415 V, 50 HZ, Ac supply , Class -F Insulation, Synchronous speed not Exceeding 3000 RPM, T.E.F.C confirming to IP:55 , of required HP suitable for the above pump ,along with flexible (LoveJoy type) coupling , coupling guard complete in all respect .
(D) Common bed plate fabricated from mild steel channel for installation of pump and Motor including anti vibration pads.
(E) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Virtual / Physical presence of Department’s representatives.
(F) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted from OEM
(G) Suitable rating DOL Starter with outdoor application as per Type-2 Coordination including Ammeter, Voltmeter, Indicating Lamps, including suitable control wiring for pressure switch as required.
(H) Pumpset to be placed on Suitable size Reinforced cement concreat (M-30) foundation with foundation bolt, Nozing Angle of size 40mm x40mm x5 mm ( Cost of RCC Foundation to be paid Extra see chapter -23 )
24.5.1 | 450 LPM with 35 mtr head | Each | 87385 | 4083
24.5.2 | 900 LPM with 35 mtr head | Each | 122746 | 5736
24.6 | Supplying, Installation, Testing & Commissioning of submersible type dewatering pump of stainless steel casing and Cast iron impellor of discharge and head given below complete with all accessories suitable for operation on 230 V, single phase/415 V /3 phase, 50 Hz. AC supply complete with starter for automatic operation including water level sensing device / float switch inter connection with submersible cable etc. as required.
24.6.1 | 180 LPM with 10 mtr head | Each | 26070 | 1218
24.7 | SITC of pressure switches of pressure range 3 to 15 Bar for Main, Jockey, Terrace pump and Diesel pumps, Etc. as Required ( Control Cable from Pressure switch to Panel to be Paid Extra ). | Each | 1845 | 111
24.8 | Providing and fixing 20/25 mm dia. (PN - 1.6, Type-S1, Flanged, ISI marked) air release valve confirming to IS - 14845 : 2000 with Double Flange isolating valve (pressure rating PN 1.6) complete with 1 no. Matching Flanges (Minimum 10 mm thick), nuts, bolts, washers, gaskets etc as required. | Each | 6635 | 278
24.9 | SITC of UL listed and FM Approved Polyethelene vane type water flow switch with actuation & delay mechanism for sensitivity in the range of 4 to 10 GPM and suitable for installation in following sizes of Sprinkler pipe for a Static pressure rating up to 250 PSI including making connections, making hole in pipe for inserting the vane, steel U bolt for mounting etc. as required.
24.9.1 | 80 mm Dia. | Each | 5493 | 222
24.9.2 | 100 mm Dia. | Each | 6681 | 278
24.9.3 | 150 mm Dia. | Each | 8139 | 333
24.10 | SITC of Pressure release valve of 50 mm dia, of CI body, with pressure setting range 7-15 kg/sqcm, on discharge header / Air Vessel, complete in all respect etc. as required. | Each | 6507 | 222
24.11 | Providing & fixing pressure transducer in M.S. Pipe line (pressure range 0 to 10 kg/cm2) suitable for 12 volts/24 volt DC. Including making connection etc. as required. ( Control Cable from Pressure Transducer to Panel to be Paid Extra ). | Each | 8376 | 389
24.12 | SITC of UL listed / FM Approved Brass Test and drain valve assembly for sprinkler system comprising of 3-position ( off, test and Drain ) ball valves with drain orifice having K-factor 5.6 and maximum working pressure 300 PSI and Inbuilt sight glass etc. as required of following size.
24.12.1 | 25 mm Dia. | Each | 5382 | 389
24.12.2 | 50 mm Dia. | Each | 11837 | 556
24.13 | Providing, Fixing, Jointing, Testing & Commissioning of Heavy duty MS 'C ' class (Heavy) pipes conforming to IS 3589 / 1239 part-I for hydrant and sprinkler applications including cutting, screwing, welding etc. & forged steel fittings like elbows, tees, tapers, reducer, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, hanger and nuts bolts including cutting hole and chase in brick walls and making good the same. complete with painting of one coat of Red Oxide and two or more coat of synthetic enamel paint of Signal red shade complete as required. (Pipe to be tested @ 10Kgf/Sqcm for 2 Hrs.).
24.13.1 | 25 mm dia | Mtr. | 400 | 111
24.13.2 | 32 mm dia | Mtr. | 514 | 139
24.13.3 | 40 mm dia | Mtr. | 598 | 167
24.13.4 | 50 mm dia | Mtr. | 833 | 222
24.13.5 | 65 mm dia | Mtr. | 1062 | 278
24.13.6 | 80 mm dia | Mtr. | 1311 | 333
24.13.7 | 100 mm dia | Mtr. | 1877 | 444
24.13.8 | 150 mm dia | Mtr. | 2771 | 667
24.13.9 | 200 mm dia, 6.0 mm thick | Mtr. | 4160 | 889
24.13.10 | 250 mm dia, 6.35 mm thick | Mtr. | 4382 | 1111
24.13.11 | 300 mm dia., 7.0 mm thick | Mtr. | 6817 | 1333
24.14 | Providing, Fixing, Jointing, Testing & Commissioning of Heavy duty MS 'C' class (Heavy) pipe conforming to IS 3589 / 1239 part-I for hydrant and sprinkler applications in Existing trench with cement concrete block as supports including cutting, welding etc & forged steel fittings like elbows, tees, tapers, reducer with cleaning,wrapping and coating of the pipe with 4 mm thick tar based polymaric corrosion protection tape including applying uniform coat of cold pipekot primer as per IS; 10221 for protection against corrosion complete in all respect. ( Pipe to be tested @ 10Kgf/Sqcm for 2 Hrs. & Excavation of Trench and refilling of trench to be paid extra).
24.14.1 | 80 mm dia | Mtr. | 1472 | 400
24.14.2 | 100 mm dia | Mtr. | 2104 | 533
24.13.3 | 150 mm dia | Mtr. | 3107 | 800
24.14.4 | 200 mm dia, 6.0 mm thick | Mtr. | 4653 | 1067
24.15 | Providing, laying, testing & commissioning of 'C' class heavy duty G.I. pipe conforming to IS 1239 including welding, Forged GI fittings like elbows, tees, tapers, nuts, bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of signal red shade complete as required. (Pipe to be tested @ 10Kgf/Sqcm for 2 Hrs.).
24.15.1 | 25 mm dia | Mtr. | 438 | 111
24.15.2 | 32 mm dia | Mtr. | 554 | 139
24.15.3 | 40 mm dia | Mtr. | 643 | 167
24.15.4 | 50 mm dia | Mtr. | 895 | 222
24.15.5 | 65 mm dia | Mtr. | 1141 | 278
24.15.6 | 80 mm dia | Mtr. | 1408 | 333
24.15.7 | 100 mm dia | Mtr. | 2012 | 444
24.15.8 | 150 mm dia | Mtr. | 2965 | 667
24.16 | Supplying and fixing cylindrical air vessel of continuous welded construction for pump room made of 450 mm dia,fabricated out of 10 mm thick dished ends and 8 mm thick MS sheet, 2000 mm in height with flanged connection, Provision for 25 mm dia drain valve,air release valve, safety valve pressure gauge as required accessories and painting with two coats of Red Oxide and two coat of Signal red enamel paint including the tank installed on suitable vertical legs. The legs shall be provided with M.S. Angle of size 75 mm x 75 mm x 5 mm at the bottom. The legs shall be grouted in cement concrete foundation. as required. ( Air Release valve, Drain valve, PRV, Pressure Gauge shall be Paid Extra ). | Each | 34904 | 2778
24.17 | Supplying and fixing cylindrical air vessel of continuous welded construction fixed at riser top made of 250 mm dia, fabricated out of 8 mm thick MS sheet, 1200 mm in height with flanged connection, Provision for 25 mm dia drain valve,air release valve,safety valve pressure gauge as required accessories and painting with two coats of Red Oxide and two coat of post office red enamel paint including The tank installed on suitable vertical legs. The legs shall be provided with M.S. Angle of size 75 mm x 75 mm x 5 mm at the bottom. The legs shall be grouted in cement concrete foundation. as required. ( Air Release valve, Drain valve, PRV, Pressure Gauge shall be Paid Extra ). | Each | 8211 | 1667
24.18 | Supplying and Fixing of PN 16 Flanged Y strainer fabricated out of cast iron body, SS 304 strainer with perforated screen with 3 mm. dia holes in existing MS / GI pipe complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets etc as required of following sizes.
24.18.1 | 80 mm dia | Each | 7772 | 667
24.18.2 | 100 mm dia | Each | 9891 | 889
24.18.3 | 150 mm dia | Each | 19804 | 1333
24.18.4 | 200 mm dia | Each | 34377 | 1778
24.18.5 | 250 mm dia | Each | 51910 | 2222
24.19 | Supplying and Fixing of PN 16 Flanged sluice valve with non rising spindle, bronze /gun metal seat confirming to IS:14846 complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
24.19.1 | 80 mm dia | Each | 10773 | 667
24.19.2 | 100 mm dia | Each | 15234 | 889
24.19.3 | 150 mm dia | Each | 23567 | 1333
24.19.4 | 200 mm dia | Each | 38181 | 1778
24.19.5 | 250 mm dia | Each | 55117 | 2222
24.20 | Providing and constructing masonry chamber 90 x 90 x 100 cms (HxWxD) inside with brick work in cement mortar 1:5 (1cement : 5fine sand) for water meter ,M.S. cover (6mmthick sheet with locking arrangement, 600 x600 with M.S. frame etc. all epoxy coated and R.C.C. top slab 1:2:4 mix(1 Cement : 2 coarsesand : 4 graded stone aggregate 20mm nominal size) including necessary excavation, back filling foundation concrete 1:5:10 mix (1 cement : 5 fine sand and 10 graded stone aggregate 20mmnominal size) leaving a pocket of 30x30 cm with out concrete and filled with pebbles andinside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick finished with a floating coat of neat cement and outside plaster finished rough complete. | Each | 20717 | 3889
24.21 | Supplying and Fixing of PN 16 Cast Iron Dual Plate Wafer Type Check Valve / Non return valve with SS / Bronze flap complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
24.21.1 | 65 mm dia | Each | 4612 | 556
24.21.2 | 80 mm dia | Each | 5273 | 667
24.21.3 | 100 mm dia | Each | 6683 | 889
24.21.4 | 150 mm dia | Each | 9072 | 1333
24.21.5 | 200 mm dia | Each | 18768 | 1778
24.22 | Supplying and Fixing of PN 16 Cast Iron swing check type reflux (Non return) Valve / Non return valve with SS / Bronze flap confirming to IS:5312 (part1) : 2004 complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
24.22.1 | 65 mm dia | Each | 9095 | 556
24.22.2 | 80 mm dia | Each | 10365 | 667
24.22.3 | 100 mm dia | Each | 13087 | 889
24.22.4 | 150 mm dia | Each | 20330 | 1333
24.22.5 | 200 mm dia | Each | 41173 | 1778
24.23 | Supplying and Fixing of PN 16 Butterfly Valve (Wafer Type) with S.G Iron Disc and confirming to IS:13095 complete with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
24.23.1 | 50 mm dia | Each | 2705 | 444
24.23.2 | 65 mm dia | Each | 3152 | 556
24.23.3 | 80 mm dia | Each | 3715 | 667
24.23.4 | 100 mm dia | Each | 4603 | 889
24.23.5 | 150 mm dia | Each | 6966 | 1333
24.23.6 | 200 mm dia Gear Operated | Each | 16023 | 1778
24.23.7 | 250 mm dia Gear Operated | Each | 23990 | 2222
24.24 | Supplying and Fixing of PN 16 Brass/GM Ball valves with screwed end, SS Ball including teflon tape etc. as required.
24.24.1 | 20 mm dia. | Each | 1095 | 111
24.24.2 | 25 mm dia. | Each | 1303 | 111
24.24.3 | 32 mm dia | Each | 2551 | 167
24.24.4 | 40 mm dia | Each | 3234 | 167
24.24.5 | 50 mm dia | Each | 4805 | 222
24.25 | Supplying and Fixing of Brass/GM gate valves with screwed end , Non rising stem and conforming to IS:778 Class-1 including teflon tape etc. as required.
24.25.1 | 20 mm dia. | Each | 1165 | 111
24.25.2 | 25 mm dia. | Each | 1750 | 167
24.25.3 | 32 mm dia | Each | 2414 | 167
24.25.4 | 40 mm dia | Each | 3323 | 222
24.25.5 | 50 mm dia | Each | 4735 | 222
24.26 | SITC of installation control valve of cast iron body and brass/bronze working parts comprising of water motor alarm, bronze seat clapper, and clapper arm, hydraulically driven mechanical gong bell to sound continous alarm when the wet riser/Sprinkler system activates, pressure gauges, emergency releases, strainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, with 2 no. Matching Flanges (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following sizes.
24.26.1 | 100 mm | Each | 42328 | 5555
24.26.2 | 150 mm | Each | 49219 | 8333
24.27 | Supplying and fixing of SS 304 Single / Double headed oblique pattern hydrant landing valve (internal/external) with 75 / 100 mm dia flanged inlet & 63 mm dia instantaneous type female outlet coupling with cast iron wheel complete with ABS cap and chain and all accessories as per IS:5290-93 (Type-A) in cluding matching flange (14 mm thick), nuts, bolts, washers, gaskets, etc as required.
24.27.1 | Single Headed with 75 mm Dia. Flanged Inlet | Each | 7528 | 556
24.27.2 | Double Headed with 100 mm Dia. Flanged Inlet | Each | 12393 | 833
24.28 | Supplying and fixing orifice plate made of 6 mm thick stainless steel with orifice of required size in between flange & landing valve of external and internal hydrant to reduce pressure to working pressure of 3.5 kg/cm2 complete with rubber gasket, GI bolts, nuts, washers etc. as required. | Each | 1543 | 56
24.29 | Supplying and fixing of flexible hose made with 100% polyester, black EPDM internal rubber lining with External coat of synthetic elastomer (IS:636, type-A) 63 mm dia, 15 mtr. Long RRL hose pipe with instanteneous type 63 mm dia SS-304 male and female couplings (IS:903) duly bound and riveted to hose pipes with copper rivets and SS wire etc. as required. | Each | 6482 | 56
24.30 | Supplying & fixing SS-304 Short Branch Pipe conforming to IS: 903:93 fitted with 20mm (nominal internal diameter) bore nozzle, for projecting water in form of solid jet. The Branch pipe shall have 63mm Male Instantaneous Inlet, suitable for use with 63 mm size Fire fighting hoses. H.P. tested to 21 kgf/cm² for 2.5 minutes. | Each | 2217 | 56
24.31 | Supplying and fixing first -Aid Fire hose reel Drum wall mounted swinging type with MS construction powder painted in post office Red, conforming to IS 884-1985 with upto date amendments, complete with the following as required. (A) Rubber Hose (B)20 mm dia UL, FM Bronze / SS nozzle with 5mm orifice (C)Drum and brackets for fixing the equipments on wall. (D) Connections from riser with 20/25 mm dia Brass/GM gate valves with screwed end and conforming to IS:778 Class-1 through Forged steel Screwed Union & M.S. pipe. Etc. as required.
0 | With 30 m x 20 mm High Pressure Braided Rubber Hose as per IS:5132 - 1969 and Bursting pressure min. 42 Kg/sqcm | Each | 10630 | 1111
24.32 | Supplying and fixing Inlet Breeching Connection of CI body with Gun Metal male instantaneous inlet couplings with Inbuilt NRV, Drainage Connection with 50 mm Brass gate valve complete with PVC blank cap and chain as required for 150mm dia Outlet with 1 no. Matching Flange (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following Ways.
24.32.1 | 2 Way | Each | 7723 | 556
24.32.2 | 3 Way | Each | 9193 | 722
24.32.3 | 4 Way | Each | 10663 | 889
24.33 | Providing and fixing of 150 mm Dia. Flanged Gun Metal Fire brigade Suction hose coupling (draw out connection) for female coupling as per IS:902-1974 complete with Matching Flange (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required. | Each | 3509 | 556
24.34 | Supply and Fixing of Cast iron body one side Flanged and other side strainer ball type foot valve with Reinforced rubber Nitrile rubber coated Ball including Matching Flange (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following Sizes.
24.34.1 | 80 mm Dia. | Each | 7801 | 556
24.34.2 | 100 mm Dia. | Each | 10464 | 772
24.34.3 | 150 mm Dia. | Each | 22718 | 889
24.34.4 | 200 mm Dia. | Each | 40520 | 1111
24.35 | Providing and Fixing of PN16 Resilient rubber lined single arch vibration eliminators suitable for raw water up to 45 deg. C temperature, working pressure 8.5 Kg/cm2 and test pressure 14 Kg/cm2 to provide relief from stresses at pipe including Matching Flange (Minimum 16 mm thick), nuts, bolts, washers, gaskets, etc as required of following Sizes.
24.35.1 | 80 mm Dia. x 150 mm OAL | Each | 67011 | 556
24.35.2 | 100 mm Dia. x 150 mm OAL | Each | 9063 | 833
24.35.3 | 150 mm Dia. x 150 mm OAL | Each | 12035 | 1111
24.36 | Supplying and fixing of 750 mm x 600 mm x 250 mm Outdoor application Fire Hose Cabinet made of 1.2 mm thick MS sheet duly powder coated in red color externally and white internally with 6 mm thick glazed doors with Expanded Metal 2 mm thick Jali including necessary locking arrangement suitable to accommodate 2 Nos 15 Mtr. Long RRL Hose and 1 No. branch pipe on Existing Wall / Angle Iron Frame as required. (Cost of MS structure for mounting Frame is to be Paid Extra) | Each | 5981 | 556
24.37 | Supplying and fixing of 1000 mm x 600 mm x 500 mm Outdoor application Fire Hose Cabinet made of 1.2 mm thick MS sheet Duly powder coated in red color externally and white internally with 6 mm thick glazed doors with Expanded Metal 2 mm thick Jali including necessary locking arrangement suitable to accommodate External hydrant with butterfly valve, 2 Nos 15 Mtr. Long RRL Hose and 1 No. branch pipe on Existing Wall / Angle Iron Frame as required. (Cost of MS structure for mounting Frame is to be Paid Extra). | Each | 15778 | 833
24.38 | Providing and fixing of Fire / Electrical Shaft Door made from powder coated (50 Micron) aluminium partialy glazed with 6 mm thick glass and Partialy / Fully Louvered with Outer frame of Aluminium Section of Size 100 mm x 45 mm x 1.5 mm and Shutter's Top, Middle & side Section of Size 82 mm x 45 mm x 1.5 mm, Bottom Section of Size 110 mm x 45 mm x 1.5 mm Complete with Hinges, Tower bolt, Handle, Aldrop, Locking Arrangement including dash fasteners of required dia and size, necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. as per drawings and the directions of Engineer-in-charge. | Each | 9505 | 1111
24.39 | Providing and Fixing of 15 mm dia Bronze quartzoid bulb type sprinkler heads with Maximum working pressure 11.6 Kg / Sqcm and suitable for 68 degree centigrade rating standard response (UL Listed) chrome plated complete in all respect of the following type.
24.39.1 | Pendant/ Upright type | Each | 315 | 83
24.39.2 | Sidewall Sprinklers (ordinary) | Each | 327 | 83
24.39.3 | Extended Throw Sidewall type . | Each | 479 | 83
24.39.4 | Concealed type with Tin alloy fusible metal plate for temperature 57 degree Centigrade | Each | 936 | 83
24.40 | Providing & fixing of UL listed 1.5 mm thick chrome plated Dual type MS Escutcheon plates fixed at junction of Sprinkler piping with the false ceiling. | Each | 131 | 28
24.41 | Supply & Fixing of Fire Man's Axe with carbon steel head & rubber moulde handle usable upto 20 KV and confirming to IS :926 with length approx 0.4 M & weight min. 1.0 Kg. | Each | 1672 | 28
24.42 | Providing & fixing sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
24.42.1 | 700 mm Long | Each | 1025 | 111
24.42.2 | 1000 mm Long | Each | 1208 | 111
24.42.3 | 1200 mm Long | Each | 1329 | 111
24.42.4 | 1500 mm Long | Each | 1512 | 111
24.43 | Providing & fixing Stainless Steel pressure gauge with dial of 150 mm dia size and range 0 to 20 kg/sq.cm with 3 / 8 " BSP bottom entry , Ball valve , SS Syphon tube all fittings etc, duly calibrated before installation in MKS and FPS units, Accuracy Level +/- 1% including Making Drilling in Existing MS Pipe Etc. as required. | Each | 1745 | 389
24.44 | Fabrication, Supply, Installation, testing and commissioning of IP-42 Electrical control panel of cubical construction, floor mounted type fabricated out of 2 mm thick CRCA sheet, compartmentalized with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 9 tank treatment process, cable alley, Interconnection with suitable size copper conductor cable / solid alum. strip strip having switchgear and accessories, mountings and internal wiring, earth terminals numbering etc. complete in all respect for main fire pump, Jockey pump and diesel pump set complete with following incoming and outgoings suitable for operation on 415 V 3 phase
24.44.1 | Incoming : 250 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 400 Amps.
Outgoing Main Fire Pump: 125 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1 Set
Outgoing Jockey Pump: 63 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1 Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. | Each | 218290 | 16665
24.44.2 | Incoming : 400 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 500 Amps.
Outgoing Main Fire Pump: 200 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1 Set
Outgoing Jockey Pump: 100 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. |  | 253035 | 16665
24.44.3 | Incoming : 630 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 800 Amps.
Outgoing Main Fire Pump: 250 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1 Set
Outgoing Jockey Pump: 125 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 1 Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. | Each | 282247 | 22220
24.44.4 | Incoming : 400 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 500 Amps.
Outgoing Main Fire Pump: 125 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Outgoing Jockey Pump: 63 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. | Each | 323499 | 27775
24.44.5 | Incoming : 630 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 800 Amps.
Outgoing Main Fire Pump: 200 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Outgoing Jockey Pump: 100 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. | Each | 394009 | 30553
24.44.6 | Incoming : 800 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, Digital Voltmeter (0-500 V) with selector switch, Digital Ammeter (0-250A) with selector switch and CTs, LED type RYB Indicating lamp, ON, OFF Trip Indicating lamps, Aluminium TPN Busbar 1000 Amps.
Outgoing Main Fire Pump: 250 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Outgoing Jockey Pump: 125 A, 50 kA, 4 pole MCCB, Ics = 100% Icu rating, with suitable HP fully automatic DOL starter as per type-2 coordination with all accessories, internal wiring required for automatic operation, Digital Ammeter with selector switch and LED type ON, OFF Trip Indicating lamp, selector switch for local/remote, auto /manual/OFF operation - 2 Set
Diesel Engine Control Panel : Comprising of Automatic / Manual selector switch and 3 attempts starting device, timers and relays as required push buttons, Start / Stop in Manual mode Indicating lamp for high / low lub. Oil pressure, High water temperature indication, Battery charger suitable for for 12V/ 24 V DC with boost and trickle selector switch, 0-30 V DC voltmeter, 0-20 A Dc ammeter, All standard accessories and relays for automatic operation of Engine
| System controller : Designing, supply Installation testing and commissioning of system controller to control operation main Electrical fire pump, jockey pump, Terrace pump in sequence as per requirement, consisting of relays, timers sensors, annunciation window for fault indication complete as required. | Each | 495637 | 33330
24.45 | SITC of UL 7th edition/ FM certified Analog addressable Multi criteria photo thermal detector with mounting base & LED etc. as required. | Each | 2725 | 167
24.46 | SITC of EN 54 / VDS certified Analog addressable Multi criteria photo thermal detector with mounting base & LED etc. as required. | Each | 2285 | 167
24.47 | SITC of UL 7th edition and FM certified photoelectric Analog addressable Smoke detector with mounting base & LED etc. as required. | Each | 2606 | 167
24.48 | SITC of EN 54 / VDS certified photoelectric Analog addressable Smoke detector with mounting base & LED etc. as required. | Each | 2118 | 167
24.49 | SITC of UL 7th edition / FM certified Analouge Addressable type Rate of Rise Heat Detectors with mounting base & LED etc. as required. | Each | 2499 | 167
24.50 | SITC of EN 54 / VDS certified Analouge Addressable type Rate of Rise Heat Detectors with mounting base & LED etc. as required. | Each | 2499 | 167
24.51 | SITC of UL 7th edition / FM certified Intelligent Addressable type loop powered auto aligned Beam detector having a coverage area with a distance of min. 5 m and max. 100 m, with auto drift compensation feature including transmitter and receiver unit with remote test features etc including the cost of all accessories, mouting arrangement Etc. as required. | Each | 82266 | 3889
24.52 | SITC of EN 54 / VDS certified Intelligent Addressable type loop powered auto aligned Beam detector having a coverage area with a distance of min. 5 m and max. 100 m, with auto drift compensation feature including transmitter and receiver unit with remote test features etc including the cost of all accessories, mouting arrangement Etc. as required. | Each | 69070 | 3889
24.53 | SITC of UL 7th edition / FM certified Addressable type fault isolator with base for isolating shorted, dewired and loose circuits between two successive fault, isolators with automatic resetting arrangement etc. as required. | Each | 2392 | 167
24.54 | SITC of EN 54 / VDS certified Addressable type fault isolator with base for isolating shorted, dewired and loose circuits between two successive fault, isolators with automatic resetting arrangement etc. as required. | Each | 2249 | 167
24.55 | SITC of UL 7th edition / FM certified Addessable Manual Call point (MCP) with LED / FIRE Indication Etc. as required. | Each | 3582 | 167
24.56 | SITC of EN 54 / VDS certified Addessable Manual Call point (MCP) with LED / FIRE Indication Etc. as required. | Each | 3320 | 167
24.57 | SITC of UL 7th edition / FM certified Addressable sounder with strobe light, Direct powered from FACP with sound level 90 dB and programmable from the panel etc. as required. | Each | 4538 | 278
24.58 | SITC of EN 54 / VDS certified Addressable sounder with strobe light, Loop powered from FACP with sound level 90 dB and programmable from the panel etc. as required. | Each | 4347 | 278
24.59 | SITC of UL 7th edition / FM certified Addressable Control (input/output) modules/ Relay / Monitor Module for shutting down lifts, control of Mechanical ventilation fans, Hooters, AHU's, Acknoledgement of Sprinkler system with potential free contact monitoring Etc. as required. | Each | 5353 | 278
24.60 | SITC of EN 54 / VDS certified Addressable control (input/output) modules/ Relay / Monitor Module for shutting down lifts, control of Mechanical ventilation fans, Hooters, AHU's, Acknoledgement of Sprinkler system with potential free contact monitoring Etc. as required. | Each | 4889 | 278
24.61 | SITC of UL 7th edition / FM certified addressable automatic fire detector for monitoring of ventilation ducts which can perform alarm pattern analysis, with even response sensitivity for all fires with smoke development with 1 no outlet tube & with 1 no. analogue addressable Photo Electric type Smoke Detector with mounting base , address switch etc. as required. | Each | 9318 | 556
24.62 | SITC of EN 54 / VDS certified addressable automatic fire detector for monitoring of ventilation ducts which can perform alarm pattern analysis, with even response sensitivity for all fires with smoke development with 1 no outlet tube & with 1 no. analogue addressable Photo Electric type Smoke Detector with mounting base , address switch etc. as required. | Each | 8492 | 556
24.63 | SITC of Response Indicator for indicating the activation of the Remotely located Detector for Addressable / Conventional type Detectors Etc. as required. | Each | 226 | 83
24.64 | SITC of EN54 / VDS certified Microprocessor based intelligent, Analogue addressable,modular, Fire Alarm Control Panel with each loop capacity of 198 detectors/devices with minimum Loop length up to 1.2 KM and 500 mA loop power as per NFPA 72 approval. The Panel shall be able to give pin point location of addressable units via the address code for each unit. The Panel shall also be able to automatically switch off all control switches when-ever any Alarm is triggered. . The panel shall have 230 + 5 % volts power supply, Automatic battery charger, 24 AH 2 x 12V, SMF Lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 30 minutes during emergency condtion. Loop interface cards, communication module, Touch screen display unit to indicate Fire / Fault Signal of individual unit, inbuilt networking port( both RS485 & Ethernet), Serial port for printer, two supervisory inputs, two position key switch and USB port for programming.including the cost of all accessories Etc. as required.
24.64.1 | 2 - Loop Panel | Each | 207386 | 16665
24.64.2 | 4 - Loop Panel Expandable upto 8 Loops | Each | 357202 | 27775
24.64.3 | Loop expansion card | Each | 73498 | 5555
24.65 | SITC of UL 7th edition / FM certified Microprocessor based inteligent, Analogue addressable,modular, Fire Alarm Control Panel with each loop capacity of 250 detectors/devices with minimum Loop length up to 2.0 KM as per NFPA 72 approval. The Panel shall be able to give pin point location of addressable units via the address code for each unit. The Panel shall also be able to automatically switch off all control switches when-ever any Alarm is triggered. . The panel shall have 230 + 5 % volts power supply, Automatic battery charger 24 AH 2 x 12V, SMF Lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 30 minutes during emergency condtion. Loop interface cards, communication module, Touch screen display unit to indicate Fire / Fault Signal of individual unit, inbuilt networking port (both RS485 & Ethernet), Serial port for printer, two supervisory inputs, two position key switch and USB port for programming. including the cost of all accessories Etc. as required.
24.65.1 | 2 - Loop Panel | Each | 2236283 | 16665
24.65.2 | 4 - Loop Panel Expandable upto 8 Loops | Each | 391879 | 27775
24.65.3 | Loop expansion card | Each | 82745 | 5555
24.66 | SITC of central; graphical fire alarm management system to centrally monitor and operate the fire alarm system as required. | Each | 134535 | 11110
24.67 | SITC of Intelligent Interface unit MODBUS, Bacnet for communication link between Fire alarm system and Building management system | Each | 104137 | 2778
24.68 | SITC of Workstation latest Intel® i7 processor, Intel Chipset motherboard, 08 GB RAM, 1 TB SATA HDD at 7200 rpm, with 2 x 4GB GPU type higher end Graphic card for H.265 compression technique with dual display ports/DVI/ HDMI port, Giga LAN Card, wireless Keyboard, wireless optical Mouse. | Each | 106359 | 5000
24.69 | SITC of UL 7th edition / FM certified Active Repeater Panel for Fire Alarm System with inbuilt networking port ( both RS485 & Ethernet ), Serial port for printer, two supervisory inputs, two position key switch and USB port for programming. The Repeater Panel shall have touch screen display unit to acknowledge, reset, silence, program, view hisory events.etc (All functions similar to main panel) The user interface of the repeater panel shall be same as the Main Controller with menu driven user interface with smart search. including the cost of all accessories Etc. as required. | Each | 131275 | 5555
24.70 | SITC of EN 54 / VDS certified Active Repeater Panel for Fire Alarm System with inbuilt networking port ( both RS485 & Ethernet ), Serial port for printer, two supervisory inputs, two position key switch and USB port for programming. The Repeater Panel shall have touch screen display unit to acknowledge, reset, silence, program, view hisory events.etc (All functions similar to main panel) The user interface of the repeater panel shall be same as the Main Controller with menu driven user interface with smart search. including the cost of all accessories Etc. as required. | Each | 108313 | 5555
24.71 | SITC of EN / LPCB certified conventional automatic fire Alarm Optical / Photoelectric type smoke detectors of photo-optic sensing chamber, 12 / 24 volt D.C., visual alarm indicator (LED's) Blink in stand by and "Steady - red" in alarm complete in all respects with base as required.including the cost of all accessories Etc. as required. | Each | 1077 | 167
24.72 | SITC of EN / LPCB certified conventional automatic fire Alarm Rate of Rise cum fixed temperature thermister type Heat Detectors , 12 / 24 volt D.C., visual alarm indicator (LED's) "Blink" in stand by and "Steady - red" in alarm complete in all respects with base as required.including the cost of all accessories Etc. as required. | Each | 1041 | 167
24.73 | SITC of EN / LPCB certified conventional photo thermal multi criteria detectors of photo-optic sensing chamber, 12 / 24 volt D.C., visual alarm indicator (LED's) "Blink " in stand by and "Steady - red" in alarm complete in all respects with base as required.including the cost of all accessories Etc. as required. | Each | 1148 | 167
24.74 | SITC of EN / LPCB certified conventional type Manual call point resettable in sheet steel / polymer housing in surface / recess complete with Glass, hammer and chain etc.including the cost of all accessories Etc. as required. | Each | 821 | 167
24.75 | SITC of EN / LPCB/ UL certified conventional type Hooter cum strobe rated 80 dB 3 mtr. for audible annunciation and 115 cd flashing at 1 Hz for visual Indication including the cost of all accessories,Etc. as required. | Each | 940 | 167
24.76 | SITC of conventional type Beam detector having a coverage area with a distance of min. 5 m and max. 100 m, including transmitter and receiver unit including the cost of all accessories,Etc. as required. | Each | 34309 | 2778
24.77 | SITC of wall type following zone (each zone accessing minimum 20 units (detectors/ devices )) Conventional Type microprocessor based with LCD display EN / LPCB/ UL listed / approved main control panel fabricated from 16 SWG CRCA sheet steel sealed maintenance free (SMF) batteries of min2X7AH of 12 V or as required.including the cost of all accessories, Etc. as required.
24.77.1 | 2 Zone | Each | 13189 | 2778
24.77.2 | 4 zone | Each | 21769 | 4444
24.77.3 | 6 zone | Each | 32399 | 5555
24.77.4 | 8 Zone | Each | 44779 | 7222
24.78 | SITC of 2 way communication Fire Fighter's Telephone Jack.Complete as required . | Each | 1599 | 111
24.79 | SITC of 2 way communication Fire Fighter's Telephone Handset to make a call to the Main FACP from Telephone Jack Location Complete as required . | Each | 10812 | 389
24.80 | Supplying and drawing Fire Resistant flexible / stranded bare copper conductor, PVC / XLPE insulated, overall aluminium mylar tape shielded ATC drain wire and outer PVC sheathed industrial Instrumentation (shielded)cables voltage grade 300/500 V as per BS /EN 50288-7 in existing surface or recessed PVC/ MS conduit/casing capping / Cable tray / Open Duct making connections, testing etc. as required. OEM Must have its own in house NABL lab setup for all testing facilities for cables.
24.80.1 | 2 x 1.5 Sq.mm Unarmoured With Outer Sheath in Red Color | Mtr. | 94 | 17
24.80.2 | 2 x 1.5 Sq.mm Armoured With Outer Sheath in Red Color | Mtr. | 141 | 28
24.81 | SITC of Voice Alarm controller with built-in USB, MP3, AM/FM player, Bluetooth v5, SD Card with PTT Mic & required zone Paging system with prerecorded messages for voice evacuation·Provides required broadcast zone output function, the peak power of each zone 1000W, 1 line input , 1 microphone input, provides mix and emergency paging output mode as required of following zone.
24.81.1 | 6 Zone | Each | 40671 | 1667
24.81.2 | 16 Zone | Each | 20218 | 2778
24.82 | SITC of power Amplifier with Amplifier topology of Class D >90% efficiency, 100V & 4-16 OHMS Transformer less design, output Short-Circuit & Thermal Protection CE Compliant with following wattage as required.
24.82.1 | 120 Watt | Each | 23977 | 1667
24.82.2 | 240 Watt | Each | 28622 | 1667
24.82.3 | 500 Watt | Each | 44112 | 1667
24.82.4 | 1000 watt | Each | 68046 | 2222
24.83 | SITC of 6W Ceiling Speaker with max SPL1M/1W 95dB . Frequency response of 80Hz-20KHz with a dispersion angle of 160 deg. The speaker should have tappings at 6W/3W/1.5W | Each | 1123 | 111
24.84 | SITC of 6W Wall mount Speaker with max SPL1M/1W 92dB . Frequency response of 160Hz-20KHz. The speaker shoud have tappings at 6W/3W/1.5W | Each | 1809 | 167
24.85 | SITC of 15W Horn Speaker (IP66) with max SPL1M/1W 115 dB . Frequency response of 350Hz-8KHz with a dispersion angle of 140 deg. The speaker shoud have tappings at 15W/7.5W | Each | 3506 | 222
24.86 | SITC of 30W Volume controller, 3/4 wire, ABS Material, with 24V Override Function | Each | 409 | 111
24.87 | Supply, Installation, Testing & Commssioning of of 8 Channel & 8 Zones IP based digital Voice Alarm controller capable of handling 4000 Watts. The voice alarm controller should be able to connect directly over Ethernet. It should have functions like the audio playing, zone control, fault monitoring, log recording, volume control and amplifier switchover. The System shall be expandable type upto 2000 Zones. Individual Voice alarm controller should also have the following functions: . 255 Priorities . Time schedule broadcasts . 2 additional Channels for back up Amplifiers. . 8 trigger inputs/outputs . 8 AVC dgital input. . 5 Addressable Noise detectors per speaker zone. | Each | 155087 | 5555
24.88 | Supply, Installation, Testing & Commssioning of IP based Networkable 7 " capacitive touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Built-in monitoring loudspeaker . Detachable goose-neck microphone . LCD touchscreen display . Audio input . Power Supply - 24VDC or POE . Provision for temporary recording function . Shortcut functions - one key broadcast, volume control etc . Shall be capable of monitoring & controlling multiple zones. | Each | 93248 | 2222
24.89 | SITC of DVD with built-in USB, MP3, AM/FM player, Bluetooth v5, SD Card Music Player with necessary accessories. | Each | 15429 | 556
24.90 | SITC of 1X500W Class-D Amplifier, which can provide automatic re-settable overcurrent, overload, overheating, overvoltage, under-voltage and DC protection and High Efficiency Class D Power Amplifier, 500W, 100V/70 Output, with 100 - 240 VAC input and 24 VDC backup power Supply | Each | 130291 | 2222
24.91 | Supply and laying following size twin parallel type Speaker cables made with multi wire, bright annealed flexible bare electrolytic grade copper conductor, insulated with specially formulated transparent grade PVC compound, red strip for identification in existing conduit etc. as required.
24.91.1 | 0.75 sq.mm | Mtr. | 27 | 3
24.91.2 | 1.0 Sq. mm | Mtr. | 33 | 4
24.91.3 | 1.5 Sq.mm | Mtr. | 52 | 7
24.91.4 | 2.5 Sq.mm | Mtr. | 71 | 9
24.92 | Supply and laying speaker cable of ollowing size 2 core twin twisted multi stranded electrolytic grade copper conductor, overall PVC insulated and armoured cable (Blue colour) on surface/ above false ceiling including cost of GI spacers, saddles etc. as required.
24.92.1 | 0.75 sq.mm | Mtr. | 88 | 11
24.92.2 | 1.0 Sq. mm | Mtr. | 97 | 12
24.92.3 | 1.5 Sq.mm | Mtr. | 117 | 14.9985
24.92.4 | 2.5 Sq.mm | Mtr. | 161 | 21
24.93 | Supply & Fixing of Water + AFFF 6% Mechanical Foam type Fire Extinguisher (Stored Pressure type) conforming to IS:15683:2018 , Powder coated Internal & External Surface Deep drawn cylinder body of Mild Steel CR2 grade conforming to IS: 513, Squeeze grip Forged brass release valve with Inbuilt safety release device, Diaphragm Type, 0 to 25 bar range pressure gauge, 450 mm long EPDM discharge tube, QR code for Product Traceability including Fixing on wall with suitable Anchor Fasteners as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted.
24.93.1 | Capacity - 6 Ltrs. | Each | 3318 | 222
24.93.2 | Capacity - 9 Ltrs. | Each | 4337 | 222
24.94 | Supply & Fixing of CO2 type Fire Extinguisher conforming to IS:15683:2018, charged with CO2 gas (purity 99.7% conforming to IS 15222), Powder coated Internal & External Surface Manganese steel ISI marked as per IS 7285 cylinder body , Wheel type Forged brass release valve ISI Marked as per IS 3224 with Inbuilt safety release device ((Fusible plug and Rupture Disc Type), 1.0 Mtr. Metal wire braided hose having minimum bursting pressure of 140 Kgf/cm2, Horn with metallic thread connection, QR code for Product Traceability, including Fixing on wall with suitable Anchor Fasteners as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted.
24.94.1 | Capacity 3.0 Kg. | Each | 6533 | 222
24.94.2 | Capacity 4.5 Kg. | Each | 7493 | 222
24.95 | Supply & Fixing of Dry Powder Agent (as per IS 4308:2019), ABC type Fire Extinguisher (Stored Pressure type) conforming to IS:15683:2018 , Powder coated Internal & External Surface Deep drawn cylinder body of Mild Steel CR2 grade conforming to IS: 513, Squeeze grip Forged brass release valve with Inbuilt safety release device, Diaphragm Type, 0 to 28 bar range pressure gauge, 450 mm long EPDM discharge tube, QR code for Product Traceability including Fixing on wall with suitable Anchor Fasteners as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted.
24.95.1 | 2 kg | Each | 2377 | 111
24.95.2 | 4 kg | Each | 3611 | 167
24.95.3 | 6 kg | Each | 4210 | 222
24.95.4 | 9 kg | Each | 5262 | 222
24.96 | Supply & Fixing of Trolley mounted 22.5 Kg CO2 type Fire Extinguisher conforming to IS: 16018:2012, charged with CO2 gas (purity 99.7% conforming to IS 15222), Powder coated Internal & External Surface Manganese steel ISI marked as per IS 7285 cylinder body , Wheel type Forged brass release valve ISI Marked as per IS 3224 with Inbuilt safety release device ((Fusible plug and Rupture Disc Type), 1.5 Mtr. long Metal wire braided hose having minimum bursting pressure of 140 Kgf/cm2, Horn with metallic thread connection, QR code for Product Traceability, including Double mounted handle as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted. | Each | 23523 | 556
24.97 | Supply & Fixing of Ceiling mounted Dry Powder Agent (as per IS 4308:2019), Modular stored pressure type ABC Fire Extinguisher , Powder coated Internal & External Surface Deep drawn cylinder body of Mild Steel CR2 grade conforming to IS: 513, Fixed Bulb with Temerature 68 deg C, QR code for Product Traceability including Fixing on Ceiling with suitable Anchor Fasteners as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted.
24.97.1 | 5 Kg Capacity | Each | 5792 | 556
24.97.2 | 10 Kg Capacity | Each | 8119 | 556
24.98 | Supply & Fixing of Ceiling mounted UL listed clean Agent (HFC-236fa), Modular type Fire Extinguisher , Powder coated Internal & External Surface Deep drawn cylinder body of Mild Steel CR2 grade conforming to IS: 513, Fixed Bulb with Temerature 68 deg C, QR code for Product Traceability including Fixing on Ceiling with suitable Anchor Fasteners as required of following capacity. Test Certificates of all the Parameters along with Hydro test & Burst test (For Cylinder Body) Certificate from OEM / External NABL Accrediated Lab is to be submitted.
24.98.1 | 5 Kg Capacity | Each | 22246 | 555
24.98.2 | 10 Kg Capacity | Each | 40458 | 555
24.99 | Supplying and Fixing of Galvanized Mild Steel fire bucket Confirming to IS: 2546 : 1974 with one coat of primer and two coat of enamel paint of approved shade on Angle Iron ( 50 x 50 x 5 mm) Stand of Size 800 x 1240 x 400 mm with MS 22 SWG Galvanized Canopy, 4 Hooks for Buckets including associated civil works etc. as required. | Set | 10214 | 1111
24.100. | Providing and fixing signages as per required content printed on photoluminescent U1000 aluminium sheet of 1.0 mm (+-10%) containing Lumigen II as base chemical, covered under UV stablized coating with suitable colour combination (Glow in dark) with high intensity properties for indoor surface glow visibility not less than 6 hrs. in total darkness and of appropriate size including fixing on wall, door, ceiling etc. with proper clamps, hangers, cleats, anchor fasteners etc. complete in all respects required.
24.100.1 | Single sided signage board | Sq.Inch | 8 | 2
24.100.2 | Double sided signage board | Sq.Inch | 13 | 3
24.101 | Providing and fixing of Aluminium housing body self contained Rechargeable LED Emergency Light with required content and Size Approx. 300 mm x 180 mm, confirming to IS:9583 :1981with Ni-Mh / Ni - Cd Battery, 3 Hrs Back Up, Constant Current Charger, Input Voltage 230 V , 50 Hz including fixing on wall, door, ceiling etc. with proper clamps, hangers, cleats, anchor fasteners etc. complete in all respects required.
24.101.1 | Single sided signage | Each | 4153 | 333
24.101.2 | Double sided signage | Each | 5069 | 333
24.102 | SITC of Electrical Driven firefighting duty Booster/ Terrace pump, Factory assembled System having One side suction , one side discharge outlet , one NRV , two isolating valves, Pressure tank, Pressure gauge, Pressure switch & OEM fitted micro-processor based panel mounted on common base frame, suitable for automatic operation and consisting of following details given as A, B, C, and D.
(A) Vertical Inline multi stage centrifugal pump complete for delivery of below mentioned discharge and Head
(B) Material of construction : Pipe Connection : Cast Iron, Pump Casing - PN-16 SS-304, Impellor - SS-304, Shaft - SS-304, Packing - Mechanical Seal
(C) Squirrel cage induction motor (IE-3 Class) suitable for 3 phase, 415 V, 50 HZ, Ac supply , Class -F Insulation, Synchronous speed not Exceeding 3000 RPM, T.E.F.C confirming to IP:55 , of required HP suitable for the above pump.
(D) Common bed plate fabricated from mild steel channel for installation of pump and Motor including anti vibration pads.
(E) The Hydrostatic tests (2 times of design operating head or 1.5 times the shut off head whichever is higher) and performance tests (to determine developed head, Pump BHP and efficiency v/s Flow) of pumps along with trip test shall be carried out at manufacturer’s works in Physical / Virtual presence of Department’s representatives. or by Third Party like RITES / PDIL / EIL
(F) Physical & Chemical Test reports of i) Pump casing (ii) Impeller (iii) Shaft (iv) Shaft sleeve and Dynamic Balance certificate is to be submitted by OEM
(G) Pumpset to be placed on Suitable size Reinforced cement concreat (M-30) foundation with foundation bolt, Nozing Angle of size 40mm x40mm x5 mm ( Cost of RCC Foundation to be paid Extra )
24.102.1 | 450 LPM with 35 mtr head | Each | 267366 | 12732
24.102.2 | 900 LPM with 35 mtr head | Each | 286464 | 13641
24.103 | Supply, assembling, errection and Installation of Sheet moulding compound (SMC) panel water tank on Existing RCC/ MS structure foundation as per IS:14399 in desired size including roof support pipe, Man hole, roof support plate, Interna & externall ladder, air vent, External bracing, Outlet / Inlet panel, over flow pipe, water level indicator etc. as Required.
24.103.1 | Tank with Height Up to 1.0 Mtr. | per Ltr. | 19 | 2
24.103.2 | Tank with Height more than 1.0 Mtr. To 3.0 Mtr. | per Ltr. | 21.6 | 2
24.103.3 | Tank with Height more than 3.0 Mtr. To 5.0 Mtr. | per Ltr. | 24.1 | 2
24.104 | Providing and fixing Hot dipped galvanized M.S fabricated puddle flange comprising of 600 mm dia long M.S class 'C' pipe with 6 mm thick M.S plates of required size including cutting holes in centre of plate, inserting pipe & making welded (Arc) joint complete. Same shall be installed with TEC welded joint in position with reinforcement bars of RCC tank wall/slab including making cutout in shuttering during concrete casting of tank of following diameter
24.104.1 | 200 mm Dia. and 400 mm plate | Set | 3456 | 567
24.104.2 | 150 mm Dia. and 400 mm plate | Set | 2765 | 453
24.104.3 | 100 mm Dia. and 300 mm plate | Set | 2212 | 363
24.104.4 | 80 mm Dia. and 300 mm plate | Set | 1728 | 283
24.104.5 | 65 mm Dia. and 300 mm plate | Set | 1383 | 227
24.104.6 | 50 mm Dia. and 300 mm plate | Set | 1175 | 193
24.105 | Refilling of following fire Extinguisher including replacement of defective parts like discharge hosepipe, nozzle,Squeeze Grip valve, lock guard or pin,pressure gauge etc.as required complete in all respect.
24.105.1 | 2 Kg ABC type | Each | 377 | 62
24.105.2 | 4 Kg ABC type | Each | 666 | 109
24.105.3 | 6 Kg ABC type | Each | 995 | 163
24.105.4 | 9 Kg ABC type | Each | 1482 | 243
24.105.5 | 3.0 Kg CO2 gas type | Each | 618 | 101
24.105.6 | 4.5 Kg CO2 gas type | Each | 911 | 149
24.105.7 | 22.5 Kg CO2 gas type | Each | 3906 | 640
24.105.8 | 6.0 ltr foam type | Each | 759 | 124
24.105.9 | 9.0 ltr foam type | Each | 1083 | 178

## Ch 25 Hire Charges
Chapter E - 25
Hire Charges for Temporary Works
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
25.1 | Hire charges for LED Flood light luminaire ( white or warm white as required )for 90- 150 watt with the standard housing ,pole & mounting accessories with wiring, connection with skilled operator to operate system etc. as and when required.
25.1.1 | With suitable pole
25.1.1.1 | for 1st day | Each/Day | 216 | 35
25.1.1.2 | For 2nd / 3rd day | Each/Day | 108 | 18
25.1.1.3 | from 4th Day onwards | Each/Day | 54 | 9
25.1.2 | Without suitable pole
25.1.2.1 | for 1st day | Each/Day | 144 | 24
25.1.2.2 | For 2nd / 3rd day | Each/Day | 72 | 12
25.1.2.3 | from 4th Day onwards | Each/Day | 36 | 6
25.1.3 | 70 watt cob light with pole
25.1.3.1 | for 1st day | Each/Day | 126 | 21
25.1.3.2 | For 2nd / 3rd day | Each/Day | 63 | 10
25.1.3.3 | from 4th Day onwards | Each/Day | 32 | 5
25.1.4 | 70 watt cob light without pole
25.1.4.1 | for 1st day | Each/Day | 85 | 13.9986
25.1.4.2 | For 2nd / 3rd day | Each/Day | 43 | 6.9993
25.1.4.3 | from 4th Day onwards | Each/Day | 21 | 3.5
25.2 | Hire charges for LED Flood light luminaire ( white or warm white as required )for 200- 250 watt with the standard housing ,pole & mounting accessories with wiring, connection with skilled operator to operate system etc. as and when required.
25.2.1 | With suitable pole
25.2.1.1 | for 1st day | Each/Day | 287 | 47
25.2.1.2 | For 2nd / 3rd day | Each/Day | 144 | 24
25.2.1.3 | from 4th Day onwards | Each/Day | 72 | 12
25.2.2 | Without suitable pole
25.2.2.1 | for 1st day | Each/Day | 216 | 35
25.2.2.2 | For 2nd / 3rd day | Each/Day | 108 | 18
25.2.2.3 | from 4th Day onwards | Each/Day | 54 | 9
25.3 | Hire charges for weather proof round LED Rope/neon flex LED / Flexible strip type LED having 2 to 5 watts/meter capacity and consisting suitable power adapter with mains , switchgear etc complete with connection with skilled operator to operate system etc. as and when required.
25.3.1 | for 1st day | Mtr/day | 7 | 1.1
25.3.2 | For 2nd / 3rd day | Mtr/day | 3 | 0.6
25.3.3 | from 4th Day onwards | Mtr/day | 2 | 0.3
25.4 | Hire charges for IP 66 protected programmable RGB LED flood light with alluminium alloy housing and having 180 degree bracket adjustment complete with driver switchgear , wiring, connection , testing etc. with skilled operator to operate system etc. as and when required.
25.4.1 | 100 watt
25.4.1.1 | for 1st day | Each/Day | 354 | 59
25.4.1.2 | For 2nd / 3rd day | Each/Day | 177 | 29.5
25.4.1.3 | from 4th Day onwards | Each/Day | 88 | 15
25.4.2 | 150 watt
25.4.2.1 | for 1st day | Each/Day | 394 | 66
25.4.2.2 | For 2nd / 3rd day | Each/Day | 197 | 33
25.4.2.3 | from 4th Day onwards | Each/Day | 99 | 16
25.4.3 | 180 watt
25.4.3.1 | for 1st day | Each/Day | 578 | 96
25.4.3.2 | For 2nd / 3rd day | Each/Day | 289 | 48
25.4.3.3 | from 4th Day onwards | Each/Day | 145 | 24
25.4.4 | 300 watt
25.4.4.1 | for 1st day | Each/Day | 816 | 136
25.4.4.2 | For 2nd / 3rd day | Each/Day | 408 | 68
25.4.4.3 | from 4th Day onwards | Each/Day | 204 | 34
25.5 | Hire Charges for LED Screen Day light type (P3.9) of suitable size for Display complete with mounting arrangement/scaffolding, masking of mounting stand, signal booster, network switch /splitter, data and power cables and sound system arrangement etc. with skilled operator to operate system etc. as and when required.
25.5.1 | for 1st day | sq.ft/ day | 177 | 30
25.5.2 | For 2nd / 3rd day | sq.ft/ day | 88 | 15
25.5.3 | from 4th Day onwards | sq.ft/ day | 44 | 7
25.6 | Hire Charges for HD Video camera suitable for SDI/HDMI output, recording in DVD/hard disk fuction complete with two operator as and when etc as required.
25.6.1 | for 1st day | Each/Day | 4624 | 771
25.6.2 | For 2nd / 3rd day | Each/Day | 2312 | 385
25.6.3 | from 4th Day onwards | Each/Day | 1156 | 193
25.7 | Hire charges for video Projection Arrangement (excluding screens) with 3 Nos. Video Camera (PWM 120 sony NX 5Z7/Equivalent) including mixer (Pansonix MX70/Data Video MX500/ Equivalent) Complete with required HDMI/SDI etc. wiring VTR, switchers, with skilled operator to operate system etc as and when required.
25.7.1 | for 1st day | Each/Day | 29985 | 4998
25.7.2 | For 2nd / 3rd day | Each/Day | 14993 | 2499
25.7.3 | from 4th Day onwards | Each/Day | 7496 | 1249
25.8 | Hire charges of Crane with operators for video camera for 360° movement complete arrangement with skilled operator to operate system as and when etc as required.
25.8.1 | for 1st day | Job/day | 8989 | 1498
25.8.2 | For 2nd / 3rd day | Job/day | 4494 | 749
25.8.3 | from 4th Day onwards | Job/day | 22477 | 375
25.9.1 | Providing Manpower through Contracting agency for Supervision / Execution / Operation of various Electromechanical Installations. (one shift of 8 working Hrs per day for 26 Working Days in a month) on basis of minimum wages + VDA order Dt. 28.03.2025 Ministry of Labour and Employement Govt. of India
25.9.1.1 | Engineer with B.Tech and1 Yrs, experience ,/Diploma Engineer with 3 Yrs. Experience in relevant field | Each Per Month |  | 25795
25.9.1.2 | Wireman, Electrician, Welder, Lineman, AC Mechanic, Fireman, , Supervisor, ELV technician or equivalent professional with ITI or Equivalent course and Experience of 2 years in relevant field ) | Each Per Month |  | 21953
25.9.1.3 | Pump Operator, AC Plant Operator, ELV System Operator, Lift Operator, DG set Operator or any other services operator with experience of 3 years in relevant field ) | Each Per Month |  | 18256
25.9.1.4 | Technical Helper Having basic Knowledge of E&M Services | Each Per Month |  | 15627
25.10 | Providing Manpower through Contracting agency for Supervision / Execution / Operation of various Electromechanical Installations. (one shift of 8 working Hrs per day ) on basis of minimum wages + VDA order Dt. 28.03.2025 Ministry of Labour and Employement Govt. of India
25.10.1.1 | Engineer with B.Tech and1 Yrs, experience ,/Diploma Engineer with 3 Yrs. Experience in relevant field | Each per Day |  | 992
25.10.1.2 | Wireman, Electrician, Welder, Lineman, AC Mechanic, Fireman, , Supervisor, ELV technician or equivalent professional with ITI or Equivalent course and Experience of 2 years in relevant field ) | Each per Day |  | 844
25.10.1.3 | Pump Operator, AC Plant Operator, ELV System Operator, Lift Operator, DG set Operator or any other services operator with experience of 3 years in relevant field ) | Each per Day |  | 702
25.10.1.4 | Technical Helper Having basic Knowledge of E&M Services | Each per Day |  | 601
25.11 | Hire charges for 42" HD LED/Plazma TV complete with mounting arrangement , connections, testing etc. with skilled operator to operate system etc as and when required.
25.11.1 | for 1st day | Job/day | 2992 | 499
25.11.2 | For 2nd / 3rd day | Job/day | 1496 | 250
25.11.3 | from 4th Day onwards | Job/day | 748 | 125
25.12 | Hire charges for 50/52"/higher sizes HD LED/Plazma TV complete with mounting arrangement , connections, testing etc.with skilled operator to operate system etc as and when required.
25.12.1 | for 1st day | Job/day | 3549 | 592
25.12.2 | For 2nd / 3rd day | Job/day | 1775 | 296
25.12.3 | from 4th Day onwards | Job/day | 887 | 148
25.13 | Hire charges for Equipments Required for Public Address & Sound System for a very important public function/ VVIP visits including transportation,T&P,Scafolding, testing and connections with trial etc. with skilled operator to operate system etc as and when required.
25.13.1 | 15 inch 3 way line Array Speaker Adamson E15/L acoustics -K1/d&b GSL or equivalent reputed make/model as approved by Engineer in charge.
25.13.1.1 | for 1st day | Each/Day | 3808 | 635
25.13.1.2 | For 2nd / 3rd day | Each/Day | 1904 | 317
25.13.1.3 | from 4th Day onwards | Each/Day | 952 | 159
25.13.2 | 12 inch 3 way line Array Speaker Adamson E12/L acoustics -K2/d&b GSL/JBL A-12 or equivalent reputed make/model as approved by Engineer in charge.
25.13.2.1 | for 1st day | Each/Day | 3386 | 564
25.13.2.2 | For 2nd / 3rd day | Each/Day | 1693 | 282
25.13.2.3 | from 4th Day onwards | Each/Day | 846.5 | 141
25.13.3 | 18 Inch dual base Adamson219/Lacoustics KS28/KSLGSUB/JBL B28 or equivalent reputed make/model as approved by Engineer in charge.
25.13.3.1 | for 1st day | Each/Day | 3386 | 564
25.13.3.2 | For 2nd / 3rd day | Each/Day | 1693 | 282
25.13.3.3 | from 4th Day onwards | Each/Day | 847 | 141
25.13.4 | Pentium -IV Laptop with HDMI cable & Stereo sound output make-HP/Dell/Lenovo or Equivalent as approved by Engineer in charge.
25.13.4.1 | for 1st day | Each/Day | 558 | 93
25.13.4.2 | For 2nd / 3rd day | Each/Day | 279 | 46
25.13.4.3 | from 4th Day onwards | Each/Day | 139.5 | 23
25.13.5 | Digital CD player consoles with built in CD players & usb drive make : pioneer or equivalent as approved by Engineer in charge.
25.13.5.1 | for 1st day | Each/Day | 2652 | 442
25.13.5.2 | For 2nd / 3rd day | Each/Day | 1326 | 221
25.13.5.3 | from 4th Day onwards | Each/Day | 663 | 111
25.13.6 | D.I. Boxes of Make Radial/BSS Ar -133 or equivalent.. as approved by Engineer in charge.
25.13.6.1 | for 1st day | Each/Day | 1061 | 177
25.13.6.2 | For 2nd / 3rd day | Each/Day | 530 | 88
25.13.6.3 | from 4th Day onwards | Each/Day | 265 | 44
25.13.7 | Cross Overs for the speakers Distributions make- DBX or equivalent as approved by Engineer in charge.
25.13.7.1 | for 1st day | Each/Day | 2652 | 442
25.13.7.2 | For 2nd / 3rd day | Each/Day | 1326 | 221
25.13.7.3 | from 4th Day onwards | Each/Day | 663 | 111
25.13.8 | Amplifier suitable for the installed speakers/sound system as required.
25.13.8.1 | for 1st day | Each/Day | 2543 | 424
25.13.8.2 | For 2nd / 3rd day | Each/Day | 1272 | 212
25.13.8.3 | from 4th Day onwards | Each/Day | 636 | 106
25.13.9 | Suspension kits with suitable stand for the 3-WAY speakers as required.
25.13.9.1 | for 1st day | Each/Day | 1115 | 186
25.13.9.2 | For 2nd / 3rd day | Each/Day | 558 | 93
25.13.9.3 | from 4th Day onwards | Each/Day | 279 | 46.5
25.13.10 | Required necessary snake cables,audio connection cables, speakers cables,electrical wiring, boards, connector etc for speakers/horns etc. as required
25.13.10.1 | for 1st day | Each/Day | 2720 | 453
25.13.10.2 | For 2nd / 3rd day | Each/Day | 1360 | 227
25.13.10.3 | from 4th Day onwards | Each/Day | 680 | 113
25.13.11 | Top Speakers JBL/RCF or equivalent. as approved by Engineer in charge.
25.13.11.1 | for 1st day | Each/Day | 21114 | 356
25.13.11.2 | For 2nd / 3rd day | Each/Day | 10557 | 178
25.13.11.3 | from 4th Day onwards | Each/Day | 529 | 89
25.13.12 | Monitor Speakers JBL/RCF or equivalent. (For Stage) as approved by Engineer in charge.
25.13.12.1 | for 1st day | Each/Day | 1265 | 211
25.13.12.2 | For 2nd / 3rd day | Each/Day | 632 | 105
25.13.12.3 | from 4th Day onwards | Each/Day | 316 | 53
25.13.13 | Cordless Mike Hi -End(For vvip visit)with antenna combiner etc.Make:-Shure .AD4D/sennheiser 6000 or equivalent.reputed make/model as approved by Engineer in charge..
25.13.13.1 | for 1st day | Each/Day | 884 | 147
25.13.13.2 | For 2nd / 3rd day | Each/Day | 442 | 74
25.13.13.3 | from 4th Day onwards | Each/Day | 221 | 36.8
25.13.14 | Cordless mike -Normal usage, with anteena combinermake- shure QLXD/sennheiser 500 or equivalent..reputed make/model as approved by Engineer in charge.
25.13.14.1 | for 1st day | Each/Day | 422 | 70
25.13.14.2 | For 2nd / 3rd day | Each/Day | 211 | 35
25.13.14.3 | from 4th Day onwards | Each/Day | 105 | 18
25.13.15 | Digital Mixer (128+48) Digico SD10/Avid S6l 24C/Dlive 7000 or equivalent..reputed make/model as approved by Engineer in charge.
25.13.15.1 | for 1st day | Each/Day | 12711 | 2140
25.13.15.2 | For 2nd / 3rd day | Each/Day | 6356 | 1070
25.13.15.3 | from 4th Day onwards | Each/Day | 3178 | 535
25.13.16 | Channel Mixer Digital (32+16) Midas M32/Sq7/ sound craft s1 or equivalent.reputed make/model as approved by Engineer in charge.
25.13.16.1 | for 1st day | Each/Day | 2962 | 499
25.13.16.2 | For 2nd / 3rd day | Each/Day | 1481 | 249
25.13.16.3 | from 4th Day onwards | Each/Day | 741 | 125
25.13.17 | Effect Processors. Make:-LSS/Behringer or equivalent as approved by Engineer in charge.
25.13.17.1 | for 1st day | Each/Day | 559 | 94
25.13.17.2 | For 2nd / 3rd day | Each/Day | 279 | 47
25.13.17.3 | from 4th Day onwards | Each/Day | 140 | 24
25.13.18 | Compressors. Make:-LSS/Behringer or equivalent as approved by Engineer in charge.
25.13.18.1 | for 1st day | Each/Day | 559 | 94
25.13.18.2 | For 2nd / 3rd day | Each/Day | 279 | 47
25.13.18.3 | from 4th Day onwards | Each/Day | 140 | 24
25.13.19 | Amplifiers 700 Watt RMS at 100 Ohm.for horns Make:-Ahuja/QSC or equivalent as approved by Engineer in charge.
25.13.19.1 | for 1st day | Each/Day | 559 | 94
25.13.19.2 | For 2nd / 3rd day | Each/Day | 279 | 47
25.13.19.3 | from 4th Day onwards | Each/Day | 140 | 24
25.13.20 | Podium Microphones. Make:-Shure/AKG /Sennheiser or equivalent as approved by Engineer in charge.
25.13.20.1 | for 1st day | Each/Day | 559 | 94
25.13.20.2 | For 2nd / 3rd day | Each/Day | 279 | 47
25.13.20.3 | from 4th Day onwards | Each/Day | 140 | 24
25.13.21 | Mikes with Big stand. Make:-Shure/AKG/Sennheiser or equivalent as approved by Engineer in charge.
25.13.21.1 | for 1st day | Each/Day | 559 | 94
25.13.21.2 | For 2nd / 3rd day | Each/Day | 279 | 47
25.13.21.3 | from 4th Day onwards | Each/Day | 140 | 24
25.13.22 | Digital Audio recorder. Make:-Cinex /Sennheiser or equivalent as approved by Engineer in charge.
25.13.22.1 | for 1st day | Each/Day | 2145 | 385
25.13.22.2 | For 2nd / 3rd day | Each/Day | 1072 | 193
25.13.22.3 | from 4th Day onwards | Each/Day | 536 | 36
25.13.23 | 32 Band Equalizer. Make:-LSS/Behringer or equivalent as approved by Engineer in charge.
25.13.23.1 | for 1st day | Each/Day | 2162 | 360
25.13.23.2 | For 2nd / 3rd day | Each/Day | 1081 | 180
25.13.23.3 | from 4th Day onwards | Each/Day | 541 | 90
25.13.24 | Snake Cable/audio cable/ BNC cable /Cat 6 cable (100 mtr) including accessories, connection, testing etc. as required.
25.13.24.1 | for 1st day | Each/Day | 462 | 77
25.13.24.2 | For 2nd / 3rd day | Each/Day | 231 | 38
25.13.24.3 | from 4th Day onwards | Each/Day | 116 | 19
25.13.25 | Optical fiber cable including accessories, connection, testing etc. as required.
25.13.25.1 | for 1st day | Per mtr/per day | 26 | 4
25.13.25.2 | For 2nd / 3rd day | Per mtr/per day | 13 | 2
25.13.25.3 | from 4th Day onwards | Per mtr/per day | 6 | 1
25.13.26 | Hire charges for table microphone with accessories. ( Delegate type ) Make-Shure/Snnheiser or equivalent as approved by Engineer in charge.
25.13.26.1 | for 1st day | Each/Day | 313 | 52
25.13.26.2 | For 2nd / 3rd day | Each/Day | 156 | 26
25.13.26.3 | from 4th Day onwards | Each/Day | 78 | 13
25.13.27 | Hire charges for lapel mic/Headhone with accessories as required. Make -shure/sennheiser or equivalent as approved by Engineer in charge.
25.13.27.1 | for 1st day | Each/Day | 816 | 136
25.13.27.2 | For 2nd / 3rd day | Each/Day | 408 | 68
25.13.27.3 | from 4th Day onwards | Each/Day | 204 | 34
25.14 | Hire charges for 500/1000 Watt halogen flood luminaire(with lamp) with skilled operator to operate system as and when etc as required.
25.14.1 | With suitable pole
25.14.1.1 | for 1st day | Each/Day | 35 | 5
25.14.1.2 | For 2nd / 3rd day | Each/Day | 18 | 3
25.14.1.3 | from 4th Day onwards | Each/Day | 9 | 1
25.14.2 | With out pole
25.14.2.1 | for 1st day | Each/Day | 20 | 3
25.14.2.2 | For 2nd / 3rd day | Each/Day | 10 | 2
25.14.2.3 | from 4th Day onwards | Each/Day | 5 | 1
25.15 | Hire charges for light point complete with lamp,holder,wiring in casing or in PVC conduit , controlling switch and circuit protection MCB's with skilled operator to operate system as and when etc as required. for shops/ stalls etc.
25.15.1 | for 1st day | Each/day | 63 | 10
25.15.2 | For 2nd / 3rd day | Each/day | 31 | 5
25.15.3 | from 4th Day onwards | Each/day | 16 | 3
25.16 | Hire charges for power/light plug on board including wiring in PVC casing or in PVC conduit , controlling switch and circuit protection MCB's with skilled operator to operate system as and when etc as required. for shops/ stalls etc.
25.16.1 | for 1st day | Each/day | 95 | 16
25.16.2 | For 2nd / 3rd day | Each/day | 48 | 8
25.16.3 | from 4th Day onwards | Each/day | 24 | 4
25.17 | Hire charges for miniature bulb with skilled operator to operate system as and when etc as required.
25.17.1 | niwar patti 60 no. 6.2 v miniature lamps.
25.17.1.1 | for 1st day | Each/Day | 12 | 2
25.17.1.2 | For 2nd / 3rd day | Each/Day | 6 | 1
25.17.1.3 | from 4th Day onwards | Each/Day | 3 | 0.5
25.17.2 | niwar patti 50 no. 0.25 v LED miniature lamps.
25.17.2.1 | for 1st day | Each/Day | 16 | 2.7
25.17.2.2 | For 2nd / 3rd day | Each/Day | 8 | 1.4
25.17.2.3 | from 4th Day onwards | Each/Day | 4 | 0.7
25.18 | Hire charges for LED tube light fixture with 18/20 watt with skilled operator to operate system as and when etc as required.
25.18.1 | for 1st day | Each/Day | 30 | 5
25.18.2 | For 2nd / 3rd day | Each/Day | 15 | 2.5
25.18.3 | from 4th Day onwards | Each/Day | 7 | 1.2
25.19 | Hire charges for LED bulb 6 watt to 13 watt of white/ warm white colour etc. mounted on wooden batten/niwar patti or in holder (with required CCT )as per choice of client or engineer in charge complete with wiring etc with skilled operator to operate system as and when etc as required.
25.19.1 | for 1st day | Each/Day | 10 | 1.6
25.19.2 | For 2nd / 3rd day | Each/Day | 5 | 0.8
25.19.3 | from 4th Day onwards | Each/Day | 2 | 0.4
25.2 | Hire charges for Silent type D.G. Set, including change over switch. Control panel, 2 No. Pipe earthing etc. and excluding POL with skilled operator to operate system as and when etc as required. of following capacity:
25.20.1 | 15 to 25 KVA
25.20.1.1 | for 1st day | Each/Day | 3128 | 521
25.20.1.2 | From 2nd day onwards | Each/Day | 1564 | 261
25.20.2 | 40 KVA
25.20.2.1 | for 1st day | Each/Day | 3944 | 657
25.20.2.2 | From 2nd day onwards | Each/Day | 1972 | 329
25.20.3 | 62.5 KVA
25.20.3.1 | for 1st day | Each/Day | 5168 | 861
25.20.3.2 | From 2nd day onwards | Each/Day | 2584 | 431
25.20.4 | 82.5 KVA
25.20.4.1 | for 1st day | Each/Day | 6119 | 1020
25.20.4.2 | From 2nd day onwards | Each/Day | 3060 | 510
25.20.5 | 125 KVA
25.20.5.1 | for 1st day | Each/Day | 8703 | 1451
25.20.5.2 | From 2nd day onwards | Each/Day | 4352 | 725
25.20.6 | 180 KVA
25.20.6.1 | for 1st day | Each/Day | 11287 | 1881
25.20.6.2 | From 2nd day onwards | Each/Day | 5643 | 941
25.20..7 | 250 KVA
25.20.7.1 | for 1st day | Each/Day | 15502 | 2584
25.20.7.2 | From 2nd day onwards | Each/Day | 7751 | 1292
25.20.8 | 500 KVA
25.20.8.1 | for 1st day | Each/Day | 21486 | 3581
25.20.8.2 | From 2nd day onwards | Each/Day | 10743 | 1791
25.21 | Hire charges of Main service line for 3 phase connection upto 50 mtr. Length (without any joint) including meter board, panel/distribution Board and supports with skilled operator to operate system as and when etc as required.
25.21.1 | Upto 25.0 sq.mm size PVC insulated and Sheathed cable( Aluminium Armoured or Un-armoured as required.)
25.21.1.1 | for 1st week | Each / week | 231 | 38
25.21.1.2 | For 2nd / 3rd day | Each / week | 116 | 19
25.21.1.3 | from 4th Day onwards | Each / week | 58 | 10
25.21.2 | above 25.0 sq.mm & upto 95 Sq.mm PVC insulated and Sheathed cable aluminium Armoured or Un-armoured as required.)
25.21.2.1 | for 1st week | Each / week | 354 | 59
25.21.2.2 | For 2nd / 3rd day | Each / week | 177 | 29
25.21.2.3 | from 4th Day onwards | Each / week | 88 | 15
25.21.3 | above95.0 sq.mm PVC insulated and Sheathed cable aluminium Armoured or Un-armoured as required.)
25.21.3.1 | for 1st week | Each / week | 626 | 104
25.21.3.2 | For 2nd / 3rd day | Each / week | 313 | 52
25.21.3.3 | from 4th Day onwards | Each / week | 156 | 26
25.22 | Hire charges of Sub service line for single/ three phase connection upto 30 mtr. Length including dist. Board and supports with skilled operator to operate system as and when etc as required.
25.22.1 | Single phase upto 6 Sqmm PVC insulated and Sheathed aluminium cable
25.22.1.1 | for 1st week | Each / week | 63 | 10
25.22.1.2 | For 2nd / 3rd day | Each / week | 31 | 5
25.22.1.3 | from 4th Day onwards | Each / week | 16 | 3
25.22.2 | Three phase & neutral upto 10 SqmmPVC insulated and Sheathed aluminium cable
25.22.2.1 | for 1st week | Each / week | 125 | 21
25.22.2.2 | For 2nd / 3rd day | Each / week | 63 | 10
25.22.2.3 | from 4th Day onwards | Each / week | 31 | 5
25.23 | Hire charges for pedestal fan of size 18" / ceiling fan of size 48"/56" sweep including connections etc.with skilled operator to operate system as and when etc as required.
25.23.1 | for 1st day | Each / day | 78 | 13
25.23.2 | For 2nd / 3rd day | Each / day | 39 | 6
25.23.3 | from 4th Day onwards | Each / day | 19 | 3
25.24 | Supply and filling of POL for DG sets | KVA / Hour | 125 | 18.768
25.25 | Hire charges for LPG Heater including commercial gas cylinder,regulator and operator with skilled operator to operate system as and when etc as required.
25.25.1 | for 1st day | Each / day | 1724 | 287
25.25.2 | For 2nd / 3rd day | Each / day | 862 | 144
25.25.3 | from 4th Day onwards | Each / day | 431 | 72
25.26 | Hire charges for Mist Fan complete with required connections and operator with skilled operator to operate system as and when etc as required.
25.26.1 | for 1st day | Each / day | 789 | 132
25.26.2 | For 2nd / 3rd day | Each / day | 394 | 66
25.26.3 | from 4th Day onwards | Each / day | 197 | 33
25.27 | Hire charges for Jumbo polycarbonate/fiber body moveable desert cooler complete with water filling and operator with skilled operator to operate system as and when etc as required.
25.27.1 | for 1st day | Each / day | 1106 | 184
25.27.2 | For 2nd / 3rd day | Each / day | 553 | 92
25.27.3 | from 4th Day onwards | Each / day | 276 | 46
25.28 | Hire charges for following type of Airconditioners including copper piping , drain piping and electrical connections with skilled operator to operate system as and when etc as required.
25.28.1 | 1.5 TR Split AC
25.28.1.1 | for 1st day | Each / day | 3332 | 555
25.28.1.2 | 2nd day onwards | Each / day | 1666 | 278
25.28.2 | 2.0 TR Split AC
25.28.2.1 | for 1st day | Each / day | 3536 | 589
25.28.2.2 | 2nd day onwards | Each / day | 1768 | 295
25.28.3 | 3.0 /4.0 TR Tower type split AC
25.28.3.1 | for 1st day | Each / day | 6867 | 1145
25.28.3.2 | 2nd day onwards | Each / day | 3434 | 572
25.28.4 | 5.0/5.5 TR ductable type Split AC
25.28.4.1 | for 1st day | Each / day | 9791 | 1632
25.28.4.2 | 2nd day onwards | Each / day | 4896 | 816
25.28.5 | 8.5 TR ductable type Split AC
25.28.5.1 | for 1st day | Each / day | 11967 | 1995
25.28.4.2 | 2nd day onwards | Each / day | 5983 | 997
25.29 | Hire charges of public address system for a important public function with 5/ 6 no. of microphones with following nos of stand Hi Fi box, speakers/ Horns, stand by amplifiers , battery backup complete including transportation etc. with skilled operator to operate system as and when etc as required. :
25.29.1 | 4 NOS 3 WAY BIG BOX SPEAKERS AND UPTO 20 HORN(5000 AUDIENCES)
25.29.1.1 | for 1st day | Each / day | 4896 | 816
25.29.1.2 | For 2nd / 3rd day | Each / day | 2448 | 408
25.29.1.3 | from 4th Day onwards | Each / day | 1224 | 204
25.29.2 | 6 NOS 3 WAY BIG BOX SPEAKERS AND UPTO 30 HORN (5000 TO 10000 AUDIENCES)
25.29.2.1 | for 1st day | Each / day | 9451 | 1575
25.29.2.2 | For 2nd / 3rd day | Each / day | 4726 | 788
25.29.2.3 | from 4th Day onwards | Each / day | 2363 | 394
25.29.3 | 8 NOS 3 WAY BIG BOX SPEAKERS AND UPTO 40 HORN (10000 TO 20000 AUDIENCES)
25.29.3.1 | for 1st day | Each / day | 13395 | 2232
25.29.3.2 | For 2nd / 3rd day | Each / day | 6697 | 1116
25.29.3.3 | from 4th Day onwards | Each / day | 3349 | 558
25.29.4 | 10 NOS 3 WAY BIG BOX SPEAKERS AND UPTO 50 HORN ( ABOVE 20000 AUDIENCES)
25.29.4.1 | for 1st day | Each / day | 17270 | 2878
25.29.4.2 | For 2nd / 3rd day | Each / day | 8635 | 1439
25.29.4.3 | from 4th Day onwards | Each / day | 4318 | 720
25.30 | Hire charges for public address system consisting of 2 Microphone with stand, Battery Backup, Amplifier,2 Loudspeakers with skilled operator to operate system as and when etc as required.
25.30.1 | for 1st day | Each / day | 1877 | 313
25.30.2 | For 2nd / 3rd day | Each / day | 938 | 156
25.30.3 | from 4th Day onwards | Each / day | 469 | 78
25.31 | Hire charges for 2 nos. 3 way Bigbox speakers with 5/6 Microphones, mixer, echo chamber, Amplifier, Battery back up with skilled operator to operate system as and when etc as required. for Musical programme.
25.31.1 | for 1st day | Each / day | 7139 | 1190
25.31.2 | For 2nd / 3rd day | Each / day | 3570 | 595
25.31.3 | from 4th Day onwards | Each / day | 1785 | 298
25.32 | Hire charges for extra battery of 12 V , 125 AH with skilled operator to operate system as and when etc as required.
25.32.1 | for 1st day | Each / day | 215 | 36
25.32.2 | For 2nd / 3rd day | Each / day | 107 | 18
25.32.3 | from 4th Day onwards | Each / day | 54 | 9
25.33 | Hire charges for cut glass chendilier of suitable no of lamps with skilled operator to operate system as and when etc as required.
25.33.1 | fr 1st day | per lamp per day | 82 | 14
25.33.2 | For 2nd / 3rd day | per lamp per day | 41 | 7
25.33.3 | from 4th Day onwards | per lamp per day | 20 | 3
25.34 | Hire charges for colour effect scanners for stage functions with skilled operator to operate system as and when etc as required.
25.34.1 | for 1st day | Each / day | 1693 | 282
25.34.2 | For 2nd / 3rd day | Each / day | 847 | 141
25.34.3 | from 4th Day onwards | Each / day | 423 | 71
25.35 | Hire charges for jumbo strove light for stage functions with skilled operator to operate system as and when etc as required.
25.35.1 | for 1st day | Each / day | 1061 | 177
25.35.2 | For 2nd / 3rd day | Each / day | 530 | 88
25.35.3 | from 4th Day onwards | Each / day | 265 | 44
25.36 | Hire charges for Back or Front Projection Screen with skilled operator to operate system as and when etc as required.
25.36.1 | for 1st day | Each / day | 462 | 77
25.36.2 | For 2nd / 3rd day | Each / day | 231 | 38
25.36.3 | from 4th Day onwards | Each / day | 116 | 19
25.37 | Hire charges for High Lumens LCD Projectors with operator ( 3500 Lumens ) and projector screen of size 8' X 6' with skilled operator to operate system as and when etc as required.
25.37.1 | for 1st day | Each / day | 2353 | 392
25.37.2 | For 2nd / 3rd day | Each / day | 1176 | 196
25.37.3 | from 4th Day onwards | Each / day | 588 | 98
25.38 | Hire charges for Medium Lumens LCD Projectors with operator ( 2500 Lumens ) and projector screen of size 8' X 6' with skilled operator to operate system as and when etc as required.
25.38.1 | for 1st day | Each / day | 1890 | 315
25.38.2 | For 2nd / 3rd day | Each / day | 945 | 158
25.38.3 | from 4th Day onwards | Each / day | 473 | 79
25.39 | Hire charges for Cable fault locator machine with manpower for detecting fault in underground cable of LT 1.1 KV grade or 11/33KV HT cable
25.39.1 | for 1st day | Each / day | 8703 | 1451
25.39.2 | for 2nd day onwartds | Each / day | 4352 | 725
25.40 | Hire charges of 1 KVA online ups with battery (backup of 1 hour at full load) with wiring,connection with skilled operator to operate system as and when required..
25.40.1 | for 1st day | Each / day | 850 | 142
25.40.2 | For 2nd / 3rd day | Each / day | 425 | 71
25.40.3 | from 4th Day onwards | Each / day | 213 | 35
25.41 | Hire charges for ceiling fan of size 48"/50" including iron rod to be fixed in aluminium dome including connection etc with skilled operator to operate system as and when required..
25.41.1 | for 1st day | Each / day | 129 | 21
25.41.2 | For 2nd / 3rd day | Each / day | 65 | 11
25.41.3 | from 4th Day onwards | Each / day | 32 | 5
25.42 | Hire charges for Aluminium truss with chain pulley and other accessories(minium height 20 ft) with skilled operator to operate system as and when required..
25.42.1 | For hanging PA system item
25.42.1.1 | for 1st day | per R.feet per day | 211 | 35
25.42.1.2 | For 2nd / 3rd day | per R.feet per day | 105 | 18
25.42.1.3 | from 4th Day onwards | per R.feet per day | 23 | 9
25.42.2 | For hanging lights only.
25.42.2.1 | for 1st day | per R.feet per day | 84 | 14
25.42.2.2 | For 2nd / 3rd day | per R.feet per day | 42 | 7
25.42.2.3 | from 4th Day onwards | per R.feet per day | 21 | 3
25.43 | Hire charges for Programmable RGBW par light(54*3)with standard housing and 180 degree bracket adjustment complete with accessories, switchgear, wiring,connection,testing etc with skilled operator to operate system as and when required..
25.43.1 | for 1st day | Each per day | 252 | 42
25.43.2 | For 2nd / 3rd day | Each per day | 126 | 21
25.43.3 | from 4th Day onwards | Each per day | 63 | 11
25.44 | Hire charges for Floor cable protector for laying Temporary cable during events made out from LPDE/PU , Each protector should be with an anti-slip textured top surface for maximum grip, should be easily linked together to create required length of following sizes.
25.44.1 | Width 135 - 200 mm x Height 25 mm (or above)
25.44.1.1 | for 1st day | Meter per day | 52 | 9
25.44.1.2 | For 2nd / 3rd day | Meter per day | 26 | 4
25.44.1.3 | from 4th Day onwards | Meter per day | 13 | 2
25.44.2 | Width 250 - 400 mm x Height 40 mm (or above)
25.44.2.1 | for 1st day | Meter per day | 110 | 18
25.44.2.2 | For 2nd / 3rd day | Meter per day | 55 | 9
25.44.2.3 | from 4th Day onwards | Meter per day | 27 | 5
Note:
1 | Rental charges will be limited to 80% of full rate of newly purchased equipment.

## Ch 26 Repairing of Coolers etc.
Chapter E -26
Repairing of Electromechanical Equipments/Items
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
26.1 | Rewinding of ceiling fan motor (starting and running winding) including all necessary material. The motor is to be wound taking no. of coils, turns and pitch as it was originally wound with required size super enamelled wire with 'E' class insulation material and making connections etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. (New model ceiling fan)
26.1.1 | 900/1200 mm sweep (New model ceiling fan) | Each | 505 | 111
26.1.2 | 1400 mm sweep (New model ceiling fan) | Each | 604 | 111
26.1.3 | All sizes (Old model ceiling fan) | Each | 1596 | 111
26.2 | Labour charges for removing and refixing of Ceiling fan/ Exhaust fan from site | Each |  | 67
26.3 | Charges for oiling, overhauling of ceiling fan, table fan, pedestal fan irrespect to the size of fan including removing,refixing of fan from site and testing etc. as required.
26.3.1 | Fans w/o Removing & Refixing | Each |  | 49.995
26.3.2 | Fans with Removing & Refixing at Suitable Location | Each |  | 117
26.4 | Providing and Replacement of ball bearing of ceiling/ exhaust fan and refixing the same at suitable location as requiredand as per OEM recommendations. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material shall be retained by the contractor. | Each | 250 | 111
26.5 | Provinding & Replacement of M.S. Shaft of ceiling fan. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 161 | 56
26.6 | P & Replacement of cover/ bearing seat of ceiling/ exhaust fan. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 139 | 56
26.7 | P & F Aluminium Blades (a set of 3 blades) duly painted and well finished 900/ 1200 mm. The material of the fan blade shall be of designation 31500B with condition HX6 aluminium alloy sheet confirming to IS 737/2008 | Each | 239 | 33
26.8 | P & F Aluminium Blades (a set of 3 blades) duly painted/ powder coated. ( 1400/ 1500 mm) The material of the fan blade shall be of designation 31500B with condition HX6 aluminium alloy sheet confirming to IS 737/2008 | Each | 317 | 33
26.9 | P & F of rubber gromet (fan insulator) | Each | 30 | 11
26.10. | Providing and Replacement of Gun metal bush of ceiling/exhaust/cooler fan/ as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 139 | 67
26.11 | P & F 3 Speed rotary switch for Desert Cooler complete with testing etc as required. | Each | 74 | 22
26.12 | P & Replacement of M.S. Shaft of fan motor for Desert Cooler/ exhaust fan. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 167 | 67
26.13 | P & replacement of supporting legs(4 no.) of vertical pump of desert cooler as required for Desert Cooler/ exhaust fan. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 94 | 22
26.14 | P & F of stud with nuts and washer for Desert Cooler/ exhaust fan.All the scrap material should be retained by the contractor. | Each | 49.995 | 22
26.15 | Servicing and overhauling of 20" sweep desert cooler including oiling, greasing, painting of tank from inside with rubber paint after properly desmantling each assembly and refixing the same as required. | Each | 250 | 89
26.16 | Painting of desert cooler with two coats of rubber paint inside of water tank and two coat of synthetic enamelled paint on both side of cooler body, fan body, grills etc.after cleaning with sand paper, complete in all respect as required. | Each | 411 | 156
26.17 | Replacement of cooler pads (heavy) set of 3 no. of size 25" x 27" | Each | 111 | 33
26.18 | P & F Brass float valve of weighing approx. 250 gm, 8" long rod,PVC ball of 4" dia. For desert coler as required. | Each | 261 | 33
26.19 | P & F adjustable M.S.grill 20/22 gauge of size approx. 24" x 26" including painting etc. as required. | Each | 378 | 56
26.20. | P & F aluminiun blade for 20'' desert cooler fan as required. | Each | 278 | 28
26.21 | P & F outer/inner threaded PVC nipple 1/2" dia and 2" long | Each | 17 | 6
26.22 | P & Replacement of pvc pipe of 1/2" size for vertical pump of desert cooler as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 42 | 6
26.23 | P & replacement of shaft for vertical pump of desert cooler as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 61 | 22
26.24 | Spray painting of ceiling fan of size 900/1200/ 1400/ 1500 mm with two coats of white/ brown enamelled paint after cleaning with sand paper. Filling etc. as required. | Each | 144 | 44
26.25 | P & replacement of 4 nos. supporting legs of 20'' fan motor with rubber pads of desert cooler as required.Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 139 | 33
26.26 | P & replacement of high quality pvc distribution ' T 'and 3 no. elbow for cooler | Each | 29.997 | 6
26.27 | P & F ISI marked waterproof plywood 6.0 mm thick including cutting, hardwares etc. as required. | Sqm. | 372 | 33
26.28 | Labour Charges for fixing of desert cooler in windows including handling of cooler upto desired location, making electrical/water connection s,testing etc. as required.
26.28.1 | Ground floor | Each |  | 106
26.28.2 | First floor | Each |  | 156
26.28.3 | Second floor | Each |  | 189
26.29 | P & F of ISI marked vertical pump suitable for 20" desert cooler including making connection testing etc. as required.
26.29.1 | ISI marked vertical pump | Each | 450 | 56
26.30. | P & F of submercible pump set suitable for 18/24 "Desert coolers. | Each | 283 | 56
26.31 | P & F of submercible pump set suitable for 36 "Desert coolers. | Each | 672 | 56
26.32 | P & F cooler fan motor suitable for 20" desert cooler including making connection testing etc. as required.
26.32.1 | with copper winding Motor ISI Marked | Each | 3477 | 111
26.32.2 | with Aluminium winding Motor ISI Marked | Each | 1928 | 111
26.33 | Rewinding of Heavy duty Exhaust fan motor including all necessary material,The motor is to be wound taking no. of coils,turns and pitch as it was originally wound with required size super enamelled wire with 'E' class insulation material and making connections etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.33.1 | 300/ 380 mm sweep | Each | 744 | 167
26.33.2 | 450 mm sweep | Each | 967 | 222
26.33.3 | 600 mm sweep | Each | 1305 | 278
26.34 | Rewinding of 400 mm table fan/pedestal fan motor including all necessary material,The motor is to be wound taking no. of coils,turns and pitch as it was originally wound with required size super enamelled wire with 'E' class insulation material and making connections etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 389 | 139
26.35 | Rewinding of single phase motor of 1400 RPM including all necessary material and of the same characteristics as original with required size of super enamelled wire 'E' class insulation material and testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.35.1 | 0.25 H.P. To 0.50 H.P. | Each | 883 | 167
26.35.2 | 0.75 H.P. To 1.0 H.P. | Each | 1217 | 194
26.35.3 | 2.0 H.P. | Each | 2011 | 333
26.36 | Rewinding of three phase squirrel cage induction motor of 1400 to 2800 RPM including all necessary material and of the same characteristics as original with required size of super enamelled wire 'E' class insulation material and testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.36.1 | 3.0 H.P. | Each | 3150 | 1111
26.36.2 | 5.0 H.P. | Each | 3911 | 1333
26.36.3 | 7.5 H.P. | Each | 4538 | 1666
26.36.4 | 10.0 H.P. | Each | 5710 | 2222
26.36.5 | 12.5 H.P. | Each | 6910 | 2778
26.36.6 | 15.0 H.P. | Each | 8666 | 3889
26.37 | Rewinding of motor of desert cooler pump with super enamelled copper wire, 'E ' class insulation material including removing,refixing,testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 222 | 111
26.38 | Rewinding of motor of desert cooler fan with super enamelled copper wire, 'E ' class insulation material including removing,refixing,testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 856 | 167
26.39 | Providing and replacement of heating element of blower type heat convector as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 117 | 22
26.40. | Providing and replacement of heating element rod of radiation type heat convector as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 111 | 22
26.41 | Providing and replacement of Chrome plated reflector of radiation type heat convector as required.Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.41.1 | single rod | Each | 117 | 33
26.41.2 | double rod | Each | 139 | 33
26.42 | Supplying and charging of fresh refrigerant and testing of performance of air conditioner/ fridge/ water cooler of following capacity including capallary and strainer/ filter.
26.42.1 | 1.0 TR Window/ Split A.C. | Each | 1472 | 444
26.42.2 | 1.5 TR Window/ Split A.C. | Each | 2042 | 500
26.42.3 | 2.0 TR Window/ Split A.C. | Each | 2611 | 556
26.42.4 | 25/50 / 40/80 Ltr. Water cooler | Each | 1583 | 556
26.42.5 | 60/120 Ltr. Water cooler | Each | 1811 | 556
26.42.6 | 150/150 Ltr. Water cooler | Each | 2083 | 778
26.42.7 | 165 Ltr Refrigerator | Each | 1194 | 444
26.42.8 | 200/210 Ltr Refrigerator | Each | 1644 | 444
26.42.9 | 280/310 Ltr Refrigerator | Each | 1972 | 556
26.43 | Replacement of defective compressor by company repaired compressor as per OEM recommendations of following gadgets including testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.43.1 | 1.0 TR A.C. | Each | 8888 | 1111
26.43.2 | 1.5 TR A.C. | Each | 9999 | 1111
26.43.3 | 2.0 TR A.C. | Each | 10555 | 1111
26.43.4 | 2.5 TR A.C. | Each | 29442 | 1111
26.43.5 | 3.0 TR A.C. | Each | 36108 | 1111
26.43.6 | 4.0 TR A.C. | Each | 41663 | 1111
26.43.7 | 25/50 / 40/80 Ltr. Water cooler | Each | 4944 | 500
26.43.8 | 60/120 Ltr. Water cooler | Each | 6611 | 500
26.43.9 | 150/150 Ltr. Water cooler | Each | 7166 | 500
26.43.10 | 165 Ltr Refrigerator | Each | 2944 | 500
26.43.11 | 200/210 Ltr Refrigerator | Each | 3555 | 500
26.43.12 | 280/310 Ltr Refrigerator | Each | 3833 | 500
26.44 | P & Replacement of condensing/ cooling coil of copper fins for following capacity A.C./ Water cooler/ Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.44.1 | 1.0 TR A.C. | Each | 2666 | 444
26.44.2 | 1.5 TR A.C. | Each | 3000 | 556
26.44.3 | 2.0 TR A.C. | Each | 3333 | 556
26.44.4 | 25/50 / 40/80 Ltr. Water cooler | Each | 2000 | 444
26.44.5 | 60/120 Ltr. Water cooler | Each | 2444 | 444
26.44.6 | 150/150 Ltr. Water cooler | Each | 2666 | 444
26.44.7 | 165 Ltr Refrigerator | Each | 1222 | 444
26.44.8 | 200/210 Ltr Refrigerator | Each | 1444 | 444
26.44.9 | 286/310 Ltr Refrigerator | Each | 1667 | 444
26.45 | Servicing of 1.0/1.5/2.0 TR capacity Split/ Window type air conditioner | Each |  | 556
26.46 | P & Replacement of overload protection of A.C./ Water cooler as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 389 | 56
26.47 | P & Replacement of thermostat of A.C./ Water cooler/fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 333 | 56
26.48 | P & Replacement of selector switch of 1.0/1.5/2.0 TR A.C Fan as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 100 | 100
26.49 | P & Replacement of starting relay of A.C/water cooler/fridge compressor as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 389 | 56
26.50. | P & Replacement of door liner of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 1000 | 222
26.51 | P & Replacement of door liner of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 1222 | 222
26.52 | P & Replacement of main liner of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 1667 | 222
26.53 | P & Replacement of main liner of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 1889 | 222
26.54 | P & Replacement of door gasket of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 194 | 83
26.55 | P & Replacement of door gasket of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 311 | 111
26.56 | P & Replacement of PVC/ acrylic vegetable basket of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 311 | 33
26.57 | P & Replacement of PVC/acrylic vegetable basket of 280/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 311 | 33
26.58 | P & Replacement of glass/acrylic cover for vegetable basket of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 228 | 33
26.59 | P & Replacement of glass/acrylic cover for vegetable basket of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 256 | 33
26.60. | P & Replacement of PVC /acrylic bottle supporter of 165/200/ 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 117 | 22
26.61 | P & Replacement of aluminium bottle supporter of 165/200/ 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 133 | 22
26.62 | P & Replacement of PVC./acrylic freezer door of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 278 | 56
26.63 | P & Replacement of PVC./acrylic freezer door of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 333 | 56
26.64 | P & Replacement of door handle of 165/200/286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 250 | 56
26.65 | P & Replacement of lamp of Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 27.8 | 11
26.66 | P & Replacement of PVC/acrylic chiller tray of 165/200 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 244 | 22
26.67 | P & Replacement of PVC/acrylic chiller tray of 286/310 Ltr. Fridge as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 272 | 22
26.68 | P & Replacement of fridge lock complete as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 172 | 22
26.69 | Spray painting of complete fridge (inside and outside ) of 165/ 200 Ltr. Capacity. | Each | 1167 | 667
26.70. | Spray painting of complete fridge (inside and outside ) of 286/310 Ltr. Capacity. | Each | 1278 | 722
26.71 | P & Replacement of fan motor of evaporator/ condensor complete as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 1722 | 167
26.72 | S & F of capacitor of 230V/ 275V, 50Hz rating of plastic casing and terminals -Lugs or copper wire.
26.72.1 | Starting capacitor
26.72.1.1 | 20-30 micro farad | Each | 124 | 22
26.72.1.2 | 40-60 micro farad | Each | 163 | 22
26.72.1.3 | 60-80 micro farad | Each | 218 | 22
26.72.1.4 | 80-100 micro farad | Each | 267 | 33
26.72.1.5 | 100-120 micro farad | Each | 300 | 33
26.72.1.6 | 120-150 micro farad | Each | 356 | 33
26.72.2 | Running capacitor
26.72.2.1 | 2.5/3.15 micro farad | Each | 44 | 11
26.72.2.2 | 4.0 micro farad | Each | 53 | 11
26.72.2.3 | 6.0 micro farad | Each | 67 | 11
26.72.2.4 | 8.0 micro farad | Each | 75 | 11
26.72.2.5 | 10.0 micro farad | Each | 87 | 11
26.72.2.6 | 15.0 micro farad | Each | 111 | 22
26.72.2.7 | 20.0 micro farad | Each | 183 | 28
26.72.2.8 | 25.0 micro farad | Each | 206 | 28
26.73 | P & Replacement of plastic/metallic sheet condensor holder suitable for ceiling fan/ exhaust fan /motor etc complete as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor. | Each | 19 | 6
26.74 | Rewinding of single phase/3phase submersible motor including all necessary material and of the same characteristics as original with required size of super enamelled wire 'E' class insulation material and testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.74.1 | 0.5 H.P. To 1.0 H.P. | Each | 3111 | 1111
26.74.2 | 2.0 H.P. | Each | 5333 | 1333
26.74.3 | Above 3.0 HP to 5.0 HP | Each | 7055 | 2000
26.74.4 | From7. 5 HP to 10.0 HP | Each | 8777 | 2778
26.75 | Repairing of submersible pump of with replacement of broken impellers ,diffuser,bush/bearing set , oil seal complete with testing etc. as required. Replacement of material or components shall be use as per guidelines of OEM of original product. All the scrap material should be retained by the contractor.
26.75.1 | 0.5 H.P. To 1.0 H.P. | Each | 2167 | 556
26.75.2 | 2.0 H.P. | Each | 3389 | 833
26.75.3 | Above 3.0 HP to 5.0 HP | Each | 4555 | 1111
26.75.4 | From7. 5 HP to 10.0 HP | Each | 5666 | 1667
26.76 | Supply and Installation of Box type EU13 Hepa Filter of 99.997% efficiency down to 0.3 micron particle size installed in zero leakage Aluminium frame as per ISO 14644-1 clean room including sealing and packing material cost like silicon and hardware cost and Labour cost for the dismantling of existing worn out filters & shifting the same to the store as required as under.
26.76.1 | 305 mm Thick | Sq Mtr | 36164 | 2366
26.76.2 | 150 mm thick | Sq Mtr | 25827 | 1690
26.77 | SITC of submersible pump of rating 18 W to 24 Watts ,minimum water discharge capacity 2800 LPH and suitable for central/large size desert cooler complete with making connections, testing etc as required. NABL accredeated / appropriated lab testing reports with OEM certificate must submitted to engineer in charge. | Each | 827 | 39
26.78 | Dismentling of split air conditioner of any capacity/any type including existing indoor unit & outdoor unit , refrigerant piping , connecting cables , drain pipe etc. including shifting of dismentaled material to store complete as required | job | 833 | 42
26.79 | Supply & fixing of evaporative cooling Celdec pads of 200mm Thick made out from impregnated cellulose paper media of imported origin including fixing in Air washer complete in all respect. | Each | 833 | 40
26.80 | Supply and fixing of ss-304 (18 guage ) made base frame with sump for 15000 to 30000 cfm double skin central evaporative cooling plant including the air cooling machine needs to be dismantal and reinstalled using a new base and sump with necessary arrengement for centrifugal fan,electric motor, wet pads , 2 nos pre-filters, 2 bend PVC eliminator.the end plates for pad & eliminator shall be in ss-304 constructed, spring isolators to be installed in this frame. | Each | 55994 | 5000
26.81 | Supply and fixing of ss-304 (18 guage ) made sump for 15000 to 30000 cfm double skin central evaporative cooling plant including the air cooling machine needs to be dismantal and reinstalled using a new sump with necessary arrengement for water pump, wet pads , 2 nos pre-filters,the end plates for pad & eliminator shall be in ss-304 constructed, include necessary hardware etc as required. | Each | 28619 | 2555
26.82 | Supply and installation of 2 bend PVC eliminator/mist eliminator with 100 mm thickness, include G.I. frame and necessary support, hardware etc as required. | Sqft | 560 | 49.995
26.83 | Supply and installation of 50 mm thick 7 layer Aluminium wiremesh pre-filter for air cooling machine/AHU etc as required. | Sqft | 560 | 49.995
26.84 | Supply and installation of 50 mm thick MERV-8 synthetic media filter with efficiency 90% to 10 microns,made in Aluminium frame for air cooling machine /AHU etc as required. | Sqft | 560 | 49.995
26.85 | Supply and installation of OEM made puf insulation panel The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm preplasticised GSS on outside and 0.80mm 275gsm plain GSS on inside complete with 25 mm thick CFC free PUF insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins.including door handles, hardwares etc as required. | Sqmt | 2489 | 222
26.86 | Providing and replacement of following ball bearing of air washer including removing the bearing and refixing the same at suitable location as required as per OEM recommendations. Replacement of material or components shall be use ae per guideline of OEM of original product. Allthe scrap material should be retained by the contractor.
26.86.1 | UC 207 | Each | 1244 | 111
26.86.2 | UC 210 | Each | 1493 | 133
26.86.3 | UC 211 | Each | 1867 | 167
26.86.4 | UC 215 | Each | 2178 | 194
26.87 | Replacement of existing transformer oil confirming to IS: 335 after removing of old oil and remove from site (old oil shall be retained by the contractor) | Liter | 120 | 7
26.88 | Charges for Testing of transformer oil for its viscosity and dielectric strength including collection of sample from top and bottom of the existing transformer tank and submission of test report complete with all T & P , labour etc as required . | Job | 2222 | 2222
26.89 | Charges for Collection , Filtration and dehydration of existing transformer oil with the help of high vaccum filtration machine and cleaning of core-coil assembly by hot oil for removal of sludge / dust particles etc. as required. | P.Ltr | 16.5 | 1
26.90 | Supply and filling of fresh transformer oil as per IS: 335 in existing transformer along with submission of oil test report for its physical and chemical properties.The oil shall be clear and free from any suspended matter or sediments complete as required complete in all respect. . | Liter | 144 | 3
26.91 | Repairing of LT/HT bushings of Distribution Transformers including replacement of brass studs , porcelain insulators , nut bolts , oil seals , gaskets etc. complete as required complete in all respect. .
26.91.1 | LT Bushing Set
26.91.1 | 63 KVA | Set | 1895 | 1111
26.91.2 | 100 KVA | Set | 2230 | 1111
26.91.3 | 160 KVA | Set | 2564 | 1111
26.91.4 | 200 KVA | Set | 3010 | 1111
26.91.5 | 250 KVA | Set | 3456 | 1111
26.91.6 | 315 KVA | Set | 3790 | 1222
26.91.7 | 400 KVA | Set | 4237 | 1389
26.91.8 | 500 KVA | Set | 5129 | 1667
26.91.9 | 630 KVA | Set | 5797 | 2222
26.91.10 | 800 KVA | Set | 8361 | 2778
26.91.11 | 1000 KVA | Set | 11148 | 3889
26.91.12 | 1250 KVA | Set | 14492 | 5555
26.91.13 | 1600 KVA | Set | 17279 | 8333
26.91.2 | HT Bushing Set
26.91.2.1 | 63 KVA to 500 KVA | Set | 2230 | 1111
26.91.2.2 | 630 KVA to 1600 KVA | Set | 3896 | 2778
26.92 | Replacement of Silica gel Breather of Distribution Transformers of following capacities complete in all respect. .
26.92.1 | 63 KVA | Set | 503 | 10
26.92.2 | 100 KVA | Set | 503 | 11
26.92.3 | 160 KVA | Set | 726 | 14
26.92.4 | 200 KVA | Set | 837 | 16
26.92.5 | 250 KVA | Set | 1114.9996 | 21
26.92.6 | 315 KVA | Set | 1227 | 24
26.92.7 | 400 KVA | Set | 1673 | 32
26.92.8 | 500 KVA | Set | 2006 | 39
26.92.9 | 630 KVA | Set | 2451 | 47
26.92.10 | 800 KVA | Set | 2488 | 54
26.92.11 | 1000 KVA | Set | 3121 | 60
26.92.12 | 1250 KVA | Set | 3344.9988 | 64
26.92.13 | 1600 KVA | Set | 3455 | 66
26.93 | Replacement of gasket of Distribution Transformers of following capacities complete in all respect. .
26.93.1 | 63 KVA to 500 KVA | Set | 1285 | 889
26.93.2 | 630 KVA to 1600 KVA | Set | 2230 | 1111

## ch 27 Solar Power Plants
Chapter E - 27
Solar Power Plants
Code No. | Description | Unit | Complete Rate without GST | ITC rate without GST
27.1 | SITC of Grid interactive Solar Photovoltaic Power Plant of required capacity having specifications as per A, B, C, D, E, F and G
A. Solar Photovoltaic module : MNRE approved and ALMM listed, SPV module of capacity 580 Wp or above, Anodized Aluminium Alloy Framed Topcon N- type Bifacial, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. , 2 mm Low Iron ARC semi-tempered glass, IP-68 PPL Junction box, 4.0 sq.mm cable with MC4 solar connector, conversion efficiency shall not be less than 21.0 % on STC, performance warranty for their output peak watt capacity > 90 % at the end of 10 years and > 80% at the end of 25 years.
B. Inverter / PCU : MPPT integrated, IGBT/MOSFET based and microprocessor/ DSP controlled Power Conditioning Unit (PCU) of AC nominal power output rating equal or greater than the required KWp of the module in IP-65 Enclosure, of 250-1500 V DC Input voltage range and 400 V AC, TPN, 50Hz +/- 2.5 Hz, Efficiency > 97%, THD < 3%, Overloading capacity > / = 10%, remote monitoring facility and PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency.
C. Module mounting structure : MMS Steel shall be as per latest IS 2062:2011 and galvanization of the mounting structure shall be in compliance of latest IS 4759, All bolts, nuts, fasteners shall be hot dip galvanized, MMS shall be designed and installed to withstand the speed for the wind zone of the location with factor of safety >1.5, STAAD report of structure to be submitted
D. Array Junction Box / DCDB : IP 65 AJB / Enclosure mounted on MMS with Polyamide glands and MC4 Connectors and cable ferrules for identification. DC fuses with SPD type-II/MOV type surge arrester to be provided.
E. ACDB : IP 65 ACDB / Enclosure mounted on MMS with Polyamide glands and MC4 Connectors and cable ferrules for identification. MCB/MCCB with SPD type-II/MOV type surge arrester to be provided.
F. Earthing and Lightning protection: The entire space occupying the SPV array shall be suitably protected against Lightning by deploying required number of Lightning Arrestors (LAs). as per NFC17-102:2011/IEC 62305 standard and three no. of Earthing with suitable size earth conductor
G. Solar meter and Cable : Laying of array cables to PCU/ DCDB unit along with supplying & fixing of necessary GI raceways/MS conduit lugs and suitable size aluminium armoured cable from ACDB to Electrical panel (up to 50 Mtr.) Discom approved solar meter (Direct or CT operated) with suitable size IP65 enclosure or MIP Box with CT
27.1.1 | 5 KWp | Set | 265247 | 5555
27.1.2 | 10 KWp | Set | 521569 | 11110
27.1.3 | 20 KWp | Set | 984436 | 19443
27.1.4 | 25 KWp | Set | 1212101 | 22220
27.1.5 | 50 KWp | Set | 2293710 | 38885
27.2 | SITC of Off Grid Hybrid Solar Photovoltaic Power Plant of required capacity having specifications as per A, B, C, D, E, F and G
A. Solar Photovoltaic module : MNRE approved and ALMM listed, SPV module of capacity 540 Wp or above, Anodized Aluminium Alloy Framed Topcon N- type Bifacial, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. , 2 mm Low Iron ARC semi-tempered glass, IP-68 PPL Junction box, 4.0 sq.mm cable with MC4 solar connector, conversion efficiency shall not be less than 21.0 % on STC, performance warranty for their output peak watt capacity > 90 % at the end of 10 years and > 80% at the end of 25 years.
B. Inverter / PCU : Power conditioning unit with MPPT inverter with combining function of inverter, MPPT solar charger and battery charge of equal or greater than the required KWp Configurable battery charging current based on applications, input voltage range for home appliances and personal computers via LCD setting, AC/Solar Charger priority , via LCD setting, Overload/ Over temperature/ short circuit protection, cold start function
C. Module mounting structure : MMS Steel shall be as per latest IS 2062:2011 and galvanization of the mounting structure shall be in compliance of latest IS 4759, All bolts, nuts, fasteners shall be hot dip galvanized, MMS shall be designed and installed to withstand the speed for the wind zone of the location with factor of safety >1.5, STAAD report of structure to be submitted
D. Array Junction Box / DCDB : IP 65 AJB / Enclosure mounted on MMS with Polyamide glands and MC4 Connectors and cable ferrules for identification. DC fuses with SPD type-II/MOV type surge arrester to be provided.
E. Battery : Lithium iron phosphate Battery 100 Ah / 48 Volts of required size
F. ACDB : IP 65 ACDB / Enclosure mounted on MMS with Polyamide glands and MC4 Connectors and cable ferrules for identification. MCB/MCCB with SPD type-II/MOV type surge arrester to be provided.
F. Earthing and Lightning protection: The entire space occupying the SPV array shall be suitably protected against Lightning by deploying required number of Lightning Arrestors (LAs). as per NFC17-102:2011/IEC 62305 standard and three no. of Earthing with suitable size earth conductor
G. Solar meter and Cable : Laying of array cables to PCU/ DCDB unit along with supplying & fixing of necessary GI raceways/MS conduit lugs and suitable size aluminium armoured cable from ACDB to Electrical panel (up to 50 Mtr.) Discom approved solar meter (Direct or CT operated) with suitable size IP65 enclosure or MIP Box with CT
27.2.1 | 5 KWp with 5 kWh Battery |  | 349955 | 5555
27.2.2 | 10 KWp with 10 kWh Battery |  | 685690 | 11110
Note 1 : | Modules deployed must use a RF identification tag. The following information must be mentioned in the RFID used on each modules. This should be inside the laminate only.
(a) | Name of the manufacture of the PV module
(b) | Name of the manufacture of Solar Cells.
(c ) | Month & year of the manufacture (separate for solar cells and modules)
(d) | Country of origin (separately for solar cells and module)
(e ) | I-V curve for the module Wattage, Im, Vm and FF for the module
(f) | Unique Serial No and Model No of the module
(g) | Date and year of obtaining IEC PV module qualification certificate.
(h) | Name of the test lab issuing IEC certificate.
(i) | Other relevant information on traceability of solar cells and module as per ISO 9001 & ISO 14001

## ch 28 Elevators
Chapter E - 28
Elevators
Code No. | Description | Unit | Complete Rate without GST
28.1 | SITC of Machine Room / Machine room less passenger / Stretcher / Bed elevator confirming to IS:17900 - part I & II and having specifications as per A, B, C, D, E, F, G, H and I
A. Doors : Centre/Telescopic opening Doors of 2100 mm height with frame made from Stainless steel grade AISI 304 2B solid (non-cladded) sheet of 1.5 mm thick in Hairline / Moonrock / honeycomb finish for car and all landing doors, The lift doors shall have 2 hour fire rating and 8 lacs cycle per year tested (with submission of necessary valid test certificate issued by NABL accredited or Independent test laboratory) with key holes and full length infared curtains and unlocking facility from outside.
B. Car : Lift car enclosure as per available lift well size and height 2300 mm made from Stainless steel grade AISI 304 2B solid (non-cladded) sheet of 1.5 mm, thick with Hairline / Moonrock / honeycomb finish with frame made from MS platform, bracing of adequate size with minimum safety factor of 5, with Toe Guard Apron, with necessary false ceiling with adequate LED lights, blower for ventilation, vinyl flooring or 20 mm recess for granite, Grab bars, mirror, emergency light ,emergency stop device, emergncy alarm, mechanical door safety, facility of auto/attendent mode. COP with SS face plate having metallic push buttons with Braille code & luminous indicator around button with FPI, scrolling UP/DN LED indicator & with / without attendant key switch, audio-visual alarm, Door closing/opening button, The lift car interior design shall be done as per the directions of engineer in charge.
C. Controller : Microprocessor/ PLC with VVVF and Regenerative Drive having closed loop control system, with IBMS compatible having necessary port. The controller shall have necessary protections such as overcurrent, overvoltage, over speed, overheat for all devices including lift motor and travel direction protection, protection for phase loss at input or output etc. various operation modes such as maintenance, change direction by attendant, full load bypass, VIP call operation, self levelling operation, call cancel facility, auto return to home landing, fireman evacuation operation, earthquake operation, door open/close operation from COP etc. The system can record information for minimum 30 latest faults, with real-time clock management and handheld keypad with LCD screen for view and setting of parameters. The control panel duly wired with proper size & strength, copper wire for power & control circuit, with provision for addition of floor/control card & allied accessories in IP-54 1.5 mm thick SS304 Enclosure
D. Motor : Lift Machine of Gearless PMSM of suitable kW with duty cycle of minimum 120 starts/hr (with submission of necessary valid test certificate issued by NABL accredited or Independent test laboratory), with Traction pulley, main hoisting flat coated steel belt / rope . OSG rope, travelling cable, electromagnetic brakes, entire assembly mounted on adequate size girders duly fixed on LMR floor/ shaft walls complete with main/diverter traction sheaves, suspension wire ropes/belts of adequate size & strength.
E. LOP : LOP with SS face plate having recess/surface push button box for all landings with scrolling UP/DN LED indicator having metallic push buttons with Braille code & luminous indicator around button with CPI, Lift car arrival & next travel direction audio-visual indication at all landings
F. Mechanical parts : adequate size 'T' section guide rails for car & counter weight with brackets fasteners, counter weight frame with necessary blocks, buffers with necessary support arrangement, MS pit ladder etc. erected with necessary steel work.
G. Other Features: Automatic rescue device with required SMF VRLA Batteries, Mechanical manual rescue device, Fireman controller having fireman switch at fire Landing, rechargeable battery operated LED emergency light in the car and along with alarm switch, Mechanical/Electronic over speed governor, Spring buffers/PU Buffers, voice annunciator, provision for CCTV, automatic car light and ventilation, false car call cancelling, Lanterns at landing,
H. Minor Civil works: such as alteration work if any necessary for erection of landing door frames and it's accessories e.g. sill, header, hole pass etc complete with plaster finish, civil work for erection buffers, erection of lift machinery, adequate size core cuts if required & scaffolding for erecting guide rails, providing and fixing steel girders/RCC work having adequate strength for mounting and hoisting lift machine, temporary barricades with caution boards at each landing to prevent accident during execution.
I. AMC & statutory permission : Comprehensive AMC of lift for 5 years including obtaining all necessary erection permissions & "License to Work the Lift" from Lift Inspector (if required)
28.1.1 | Lift with travelling speed 1.0 Mtr./ Second and 2 stops
28.1.1.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1048816
28.1.1.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1160864
28.1.1.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1297666
28.1.1.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1422742
28.1.1.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1569967
28.1.1.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2005825
28.1.1.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 2436380
28.1.2 | Lift with travelling speed 1.0 Mtr./ Second and 3 stops
28.1.2.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1123080
28.1.2.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1235128
28.1.2.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1378444
28.1.2.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1513943
28.1.2.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1670289
28.1.2.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2114570
28.1.2.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 2547125
28.1.3 | Lift with travelling speed 1.0 Mtr./ Second and 4 stops
28.1.3.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1198647
28.1.3.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1310695
28.1.3.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1460525
28.1.3.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1602539
28.1.3.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1768004
28.1.3.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2221406
28.1.3.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 2466377
28.1.4 | Lift with travelling speed 1.0 Mtr./ Second and 5 stops
28.1.4.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1272911
28.1.4.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1384959
28.1.4.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1543259
28.1.4.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1693740
28.1.4.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1863114
28.1.4.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2165806
28.1.4.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 2565759
28.1.5 | Lift with travelling speed 1.0 Mtr./ Second and 6 stops
28.1.5.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1348478
28.1.5.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1460525
28.1.5.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1511338
28.1.5.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1657987
28.1.5.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1825240
28.1.5.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2266400
28.1.5.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 2666353
28.1.6 | Lift with travelling speed 1.5 Mtr./ Second and 7 stops
28.1.6.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1420136
28.1.6.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1436794
28.1.6.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1650715
28.1.6.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 1797365
28.1.6.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 1964618
28.1.6.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2651355
28.1.6.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3081305
28.1.7 | Lift with travelling speed 1.5 Mtr./ Second and 8 stops
28.1.7.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1569967
28.1.7.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1687226
28.1.7.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1728282
28.1.7.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 2022065
28.1.7.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 2208377
28.1.7.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2794672
28.1.7.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3224621
28.1.8 | Lift with travelling speed 1.5 Mtr./ Second and 9 stops
28.1.8.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1648140
28.1.8.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1760187
28.1.8.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 1939984
28.1.8.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 2110661
28.1.8.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 2307396
28.1.8.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 2937988
28.1.8.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3367938
28.1.9 | Lift with travelling speed 1.5 Mtr./ Second and 10 stops
28.1.9.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1602236
28.1.9.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1830543
28.1.9.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 202265
28.1.9.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 2201863
28.1.9.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 2403808
28.1.9.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 3081305
28.1.9.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3266283
28.1.10. | Lift with travelling speed 1.5 Mtr./ Second and 11 stops
28.1.10.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1797971
28.1.10.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1910018
28.1.10.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 2104147
28.1.10.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 2293064
28.1.10.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 2501524
28.1.10.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 3224621
28.1.10.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3654571
28.1.11 | Lift with travelling speed 1.5 Mtr./ Second and 12 stops
28.1.11.1 | 6 passengers/408 Kg, Landing Door 750 mm wide | Each | 1871871
28.1.11.2 | 8 passengers/544 Kg , Landing Door 800 mm wide | Each | 1985585
28.1.11.3 | 10 passengers/680 Kg , Landing Door 800 mm wide | Each | 2187531
28.1.11.4 | 13 passengers/884 Kg , Landing Door 900/1000 mm wide | Each | 2381660
28.1.11.5 | 15 passengers/1020 Kg , Landing Door 900/1000 mm wide | Each | 2599240
28.1.11.6 | 20 passengers/1360 Kg , Stretcher/Hospital Elevator with Landing Door 1100/1200 mm wide | Each | 3367938
28.1.11.7 | 26 passengers/1768 Kg, Hospital Bed Elevatorwith Landing Door 1200 mm wide | Each | 3797887
28.2 | SITC of Machine Room / Machine room less Freight/ Goods elevator with travelling speed 0.5 mtr. / second confirming to IS:17900 - part I & II and having specifications as per A, B, C, D, E, F, G, H and I
A. Doors : Centre 4 panel /Telescopic opening Doors of 2100 mm height with frame made from Stainless steel grad e AISI 304 2B solid (non-cladded) sheet of 1.5 mm thick in honeycomb finish for car and all landing doors, The lift doors shall have 1 hour fire rating and 8 lacs cycle per year tested (with submission of necessary valid test certificate issued by NABL accredited or Independent test laboratory) with key holes and full length infared curtains and unlocking facility from outside.
B. Car : Point load designed Lift car enclosure as per available lift well size and height 2300 mm made from Stainless steel grade AISI 304 2B solid (non-cladded) sheet of 1.5 mm, thick with honeycomb finish with frame made from MS platform, bracing of adequate size with minimum safety factor of 5, with Toe Guard Apron, with necessary false ceiling with adequate LED lights, Fan for ventilation, 5 mm thick aluminium chequered plate floor, Grab bars, emergency light ,emergency stop device, emergncy alarm, mechanical door safety, facility of auto/attendent mode. COP with SS face plate having metallic push buttons with Braille code & luminous indicator around button with FPI, scrolling UP/DN LED indicator & with / without attendant key switch, audio-visual alarm, Door closing/opening button. The lift car interior design shall be done as per the directions of engineer in charge.
C. Controller : Microprocessor/ PLC with VVVF and Regenerative Drive having closed loop control system, with IBMS compatible having necessary port. The controller shall have necessary protections such as overcurrent, overvoltage, over speed, overheat for all devices including lift motor and travel direction protection, protection for phase loss at input or output etc. various operation modes such as maintenance, change direction by attendant, full load bypass, VIP call operation, self levelling operation, call cancel facility, auto return to home landing, fireman evacuation operation, earthquake operation, door open/close operation from COP etc. The system can record information for minimum 30 latest faults, with real-time clock management and handheld keypad with LCD screen for view and setting of parameters. The control panel duly wired with proper size & strength, copper wire for power & control circuit, with provision for addition of floor/control card & allied accessories in IP-54 1.5 mm thick SS304 Enclosure
D. Motor : Lift Machine of Gearless PMSM of suitable kW with duty cycle of minimum 120 starts/hr (with submission of necessary valid test certificate issued by NABL accredited or Independent test laboratory), with Traction pulley, main hoisting flat coated steel belt / rope . OSG rope, travelling cable, electromagnetic brakes, entire assembly mounted on adequate size girders duly fixed on LMR floor/ shaft walls complete with main/diverter traction sheaves, suspension wire ropes/belts of adequate size & strength.
E. LOP : LOP with SS face plate having recess/surface push button box for all landings with scrolling UP/DN LED indicator having metallic push buttons with Braille code & luminous indicator around button with CPI, Lift car arrival & next travel direction audio-visual indication at all landings
F. Mechanical parts : adequate size 'T' section guide rails for car & counter weight with brackets fasteners, counter weight frame with necessary blocks, buffers with necessary support arrangement, MS pit ladder etc. erected with necessary steel work.
G. Other Features: Automatic rescue device with required SMF VRLA Batteries, Fireman controller having fireman switch at fire Landing, rechargeable battery operated LED emergency light in the car and along with alarm switch, Mechanical/Electronic over speed governor, Spring buffers/PU Buffers, voice annunciator, provision for CCTV, automatic car light and ventilation, false car call cancelling, Lanterns at landing,
H. Minor Civil works: such as alteration work if any necessary for erection of landing door frames and it's accessories e.g. sill, header, hole pass etc complete with plaster finish, civil work for erection buffers, erection of lift machinery, adequate size core cuts if required & scaffolding for erecting guide rails, providing and fixing steel girders/RCC work having adequate strength for mounting and hoisting lift machine, temporary barricades with caution boards at each landing to prevent accident during execution.
I. AMC & statutory permission : Comprehensive AMC of lift for 5 years including obtaining all necessary erection permissions & "License to Work the Lift" from Lift Inspector (if required)
28.2.1 | 2000 Kg Lift with Door opening 1400 mm
28.2.1.1 | 2 stop Freight Elevator | Each | 2866330
28.2.1.2 | 3 stop Freight Elevator | Each | 2964046
28.2.1.3 | 4 stop Freight Elevator | Each | 3061761
28.2.1.4 | 5 stop Freight Elevator | Each | 3159477
28.2.1.5 | 6 stop Freight Elevator | Each | 3257193
28.2.1.6 | 7 stop Freight Elevator | Each | 3354909
28.2.1.7 | 8 stop Freight Elevator | Each | 3452625
28.2.1.8 | 9 stop Freight Elevator | Each | 3550340
28.2.1.9 | 10 stop Freight Elevator | Each | 3648056
28.2.1.10 | 11 stop Freight Elevator | Each | 3745772
28.2.1.11 | 12 stop Freight Elevator | Each | 3843488
28.2.2 | 3000 Kg Lift with Door opening 1800 mm
28.2.2.1 | 2 stop Freight Elevator | Each | 2996618
28.2.2.2 | 3 stop Freight Elevator | Each | 3094333
28.2.2.3 | 4 stop Freight Elevator | Each | 3192049
28.2.2.4 | 5 stop Freight Elevator | Each | 3289765
28.2.2.5 | 6 stop Freight Elevator | Each | 3387481
28.2.2.6 | 7 stop Freight Elevator | Each | 3485197
28.2.2.7 | 8 stop Freight Elevator | Each | 3582912
28.2.2.8 | 9 stop Freight Elevator | Each | 3680628
28.2.2.9 | 10 stop Freight Elevator | Each | 3778344
28.2.2.10 | 11 stop Freight Elevator | Each | 3876060
28.2.2.11 | 12 stop Freight Elevator | Each | 3973776
28.2.3 | 4000 Kg Lift with Door opening 1800 mm
28.2.3.1 | 2 stop Freight Elevator | Each | 3126905
28.2.3.2 | 3 stop Freight Elevator | Each | 3224621
28.2.3.3 | 4 stop Freight Elevator | Each | 3322337
28.2.3.4 | 5 stop Freight Elevator | Each | 3420053
28.2.3.5 | 6 stop Freight Elevator | Each | 3517768
28.2.3.6 | 7 stop Freight Elevator | Each | 3615484
28.2.3.7 | 8 stop Freight Elevator | Each | 3713200
28.2.3.8 | 9 stop Freight Elevator | Each | 3810916
28.2.3.9 | 10 stop Freight Elevator | Each | 3908632
28.2.3.10 | 11 stop Freight Elevator | Each | 4006347
28.2.3.11 | 12 stop Freight Elevator | Each | 4104063
28.3 | SITC of Duplex Lift control system for two nos. microprocessor/PLC based each simplex lift controllers along with necessary software with programming and hardware e. g. logic board, necessary communication/control/data cabling laying in rigid PVC conduits/trunking etc. complete. as required. | Each | 28014
28.4 | SITC of Triplex Lift control system for three nos. microprocessor/PLC each based simplex lift controllers along with necessary software with programming and hardware e.g. logic board, necessary communication/control/data cablinglaying in rigid PVC conduits/trunking etc. complete as required. | Each | 33283
28.5 | Dismantling the existing 6 to 10 Passenger lift of all types travelling upto 6 floors having with auto/manual operated doors for lift car & all landings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original on buy back basis | Each | -34031
28.6 | Dismantling the existing 13 to 20 Passenger lift of all types travelling upto 6 floors having with auto/manual operated doors for lift car & all landings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original this job on buy back basis | Each | -43999
28.7 | Dismantling the existing 26 Passenger lift of all types travelling upto 6 floors having with auto/manual operated doors for lift car & all andings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original on buy back basis | Each | -53967
28.8 | Dismantling the existing 6 to 10 Passenger lift of all types travelling from 7 to 12 floors having with auto/manual operated doors for lift car & all landings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original on buy back basis | Each | -43999
28.9 | Dismantling the existing 13 to 20 Passenger lift of all types travelling from 7 to 12 floors having with auto/manual operated doors for lift car & all landings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original on buy back basis | Each | -53967
28.10. | Dismantling the existing 26 Passenger lift of all types travelling from 7 to 12 floors having with auto/manual operated doors for lift car & all landings with door frames, guide rails, controller, wiring buffers, Lift Machine, ropes complete with all allied accessories of Lift and making the site clear in all respect complete with refilling the holes with cement mortar & making the site as original on buy back basis | Each | -69204
28.11 | Add Extra for Glass Landing door panels with 1 Hour fire rating in place of Solid doors Landing Doors and Car doors of following Size
28.11.1 | 2100 mm x 750/800 mm | per Door | 75439
28.11.2 | 2100 mm x 900/1000 mm | per Door | 96517
28.11.3 | 2100 mm x 1100/1200 mm | per Door | 117595
Note:
1 | To ensure the performance of the lifts, the OEM must have its in House Testing Tower facility with minimum 20 mtr. Height and OEM must have atleast 3 service centers in Rajasthan.
2 | If the lift shaft is greater than the required size of the lift as mentioned in relevant Indian Standard [with Amendments up to date], the provision of extra steel required for erecting supports of guide rails shall be made as a separate item.
3 | The Electrical power supply of 3 phase, 415 V, 50 Hz and Bulk head Lights, power points, separate cables for lighting and power & shall be erected through lift shaft only with 2 nos distinct earth connections from lift machine & controller .as per Lift OEM requirement shall be made available as separate item.
4 | The Traffic Analysis [TA] shall be done as per the provisions laid down in relevant Indian standards for finalizing the capacity and number of Lifts in different types of buildings.
5 | During Civil construction of building, It shall be ensured that Lift shaft of suitable size is constructed with RCC (Except the Entrance wall which is to be constructed with 225 mm bricks) including plaster with white wash and properly ventilated machine room / Lift shaft, Water proofing in lift pit, provision of hoisting beam / hook above the lift well and Trap door, Architrave work at lift entrance etc.
6 | Cost of Duplex / Triplex (if required) is included in cost of lift , no Extra cost will be paid
7 | Lift construction and safety features of the lifts should confirm to IS:17900

## Ch 29 AMC
Chapter E - 29
AMC of Electromechanical Services
Code No. | Description | Unit | Complete Rate without GST
29.1 | All in all comprehensive maintenance of the passenger /bed cum stretcher /goods elevator having various speed as per OEM guidelines and maintenance manual including car with all car accessories , hoist way accessories and complete with machine room /MRL accessories including replacement of diffused battery bank of ARD system as per following details .
29.1.1 | 6 Passenger , 408 Kg Elevator up to 5 Stops | Job per Month | 7835
29.1.2 | 8 Passenger , 544 Kg Elevator up to 5 Stops | Job per Month | 8436
29.1.3 | 10 Passenger , 680 Kg Elevator up to 5 Stops | Job per Month | 9040
29.1.4 | 13 Passenger , 884 Kg Elevator up to 5 Stops | Job per Month | 10246
29.1.5 | 15/16 Passenger , 1020/1088 Kg Elevator up to 5 Stops | Job per Month | 11037
29.1.6 | 20 Passenger , 1360 Kg Elevator up to 5 Stops | Job per Month | 13920
29.1.7 | 26 Passenger , 1768 Kg Elevator up to 5 Stops | Job per Month | 17849
29.1.8 | 1000 Kg Goods Elevator up to 5 Stops | Job per Month | 10776
29.1.9 | 1500 Kg Goods Elevator up to 5 Stops | Job per Month | 12610
29.1.10 | 6 Passenger , 408 Kg Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 300
29.1.11 | 8 Passenger , 544 Kg Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 323
29.1.12 | 10 Passenger , 680 Kg Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 346
29.1.13 | 13 Passenger , 884 Kg Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 392
29.1.14 | 15/16 Passenger , 1020/1088 Kg Elevatorabove 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 441
29.1.15 | 20 Passenger , 1360 Kg Elevatorabove 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 557
29.1.16 | 26 Passenger , 1768 Kg Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 714
29.1.17 | 1000 Kg Goods Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 431
29.1.18 | 1500 Kg Goods Elevator above 5 Stops per stop (Add for each additional stop above five stops) | Job per Month | 504
29.2 | All in all comprehensive maintenance of 11/0.415 KV or 33/0.415 KV Distribution sub station including 11 KV circuit Breaker , Transformer and its complete accessories , Auto transfer switch ,repairing of LT/HT cables with terminations, LT panel with complete accessories , Sub station Earthings etc with maintaining of Log Books complete in all respect but excluding of transformer oil as and when required.
29.2.1 | Substation Up to 500 KVA rating Transformer | Job per KVA per Month | 9.999
29.2.2 | Substation Above 500 KVA Transformer | Job per KVA per Month | 13
29.2.3 | Substation with 33/11 KV Transformer | Job per KVA per Month | 14
29.3 | All in all comprehensive maintenance including servicing , replacement of fuel - filter, coolant , lubricating oil etc of Diesel Generating set including auto mains failure (AMF) panel , change over switch , earthing etc as per OEM guidelines and maintenance manual complete in all respet. (Excluding replacement of batteries as and when required.)
29.3.1 | Up to 62.5 KVA D. G. Set | Job per KVA per Month | 29
29.3.2 | Above 62.5 KVA | Job per KVA per Month | 37
29.3.3 | OEM approved liquid urea for BS-IV type DG Set | Per litre | 172
29.4 | All in all comprehensive maintenance of Automatic power factor correction panel including repair / replacement of defective componenets to maintain the power factor as per Discom's permissible limit and without any penalty or surcharge.
29.4.1 | Up to 125 KVAR APFC Panels | Job per KVAR per Month | 44.9955
29.4.2 | Above 125 kvar APFC Panels | Job per KVAR per Month | 58
29.5 | All in all General servicing and cleaning of various type airconditioners During Defect Laibility Period of Equipments including compressor, condensing/ cooling coil , refrigerant piping , fan motor , remote , charging of refrigerant when ever required as per OEM's recommendations to meet out the efficient performance of the equipment.
29.5.1 | 1.0/1.5/2.0 Tr window type air conditioner | Job per year | 928
29.5.2 | 1.5/1.8/2.0 Tr Split type air conditioner | Job per year | 1544
29.5.3 | 1.5/1.8/2.0 Tr Split A.C.'s with Invertor Technology/ Hot & cold technology | Job per year | 1700
29.5.4 | 2.2/3.0/3.6/4.2 Tr Floor Standing Tower Type Split A.C. | Job per year | 2822
29.5.5 | 1.5/2.0/3.0/4.0 Tr Cassette type Split type air conditioner | Job per year | 3094
29.5.6 | 3.0/4.0/5.0 Tr Ductable type Split type air conditioner | Job per year | 4455
29.6 | All in all comprehensive maintenance of various type air conditioners including repair / replacement of compressor, condensing/ cooling coil , refrigerant piping , fan motor , remote , charging of refrigerant whenever required and periodical servicing as per OEM's recommendations and standard terms & conditions of PWD to meet efficient performance of the equipment.
29.6.1 | 1.0/1.5/2.0 Tr window type air conditioner | Job per year | 1850
29.6.2 | 1.5/1.8/2.0 Tr Split type air conditioner | Job per year | 3089
29.6.3 | 1.5/1.8/2.0 Tr Split type air conditioner with inverter technology/hot&cold technology. | Job per year | 3394
29.6.4 | 2.2/3.0/3.6/4.2 Tr Floor Standing Tower Type Split A.C. | Job per year | 5666
29.6.5 | 1.5/2.0/3.0/4.0 Tr Cassette type Split type air conditioner | Job per year | 6172
29.6.6 | 3.0/4.0/5.0 Tr Ductable type Split type air conditioner | Job per year | 7405
29.7 | All in all General servicing and cleaning of various type of Water cooler During Defect Laibility Period of Equipment including compressor, condensing/ cooling coil ,water tank with inner piping including charging of refrigerants when ever required , cleaning , servicing etc as per OEM's recommendations to meet out the efficient performance of the equipment.
29.7.1 | Up to 60/120 Ltr capacity | Job per year | 1233
29.7.2 | 150/150 Ltr capacity | Job per year | 1700
29.7.3 | 150/400 Ltr to 225/400 Ltr capacity | Job per year | 2478
29.7.4 | Water Chiller of capacity 1200 Ltrs/hr cooling Capacity and 500 Ltrs Storage Capacity | Job per year | 13888
29.8 | All in all comprehensive maintenance of Water cooler including compressor, condensing/ cooling coil ,water tank with inner piping including repair / replacement of components like filters, membrane, charging of refrigerants whenever required , cleaning , servicing etc. as per OEM's recommendations and standard terms & conditions of PWD to meet efficient performance of the equipment.
29.8.1 | Up to 60/120 Ltr capacity | Job per year | 2478
29.8.2 | 150/150 Ltr capacity | Job per year | 3400
29.8.3 | 150/400 Ltr to 225/400 Ltr capacity | Job per year | 4966
29.8.4 | Water Chiller of capacity 1200 Ltrs/hr cooling Capacity and 500 Ltrs Storage Capacity | Job per year | 27775
29.9 | All in all comprehensive maintenance of Reverse Osmosis water purification system including repair / replacement of components ,consumables , cleaning , servicing etc as per OEM's Guide lines to meet out the TDS level of Water as per client requirement / standard norms to meet efficient performance of the equipment.
29.9.1 | 12-15 Ltr/hr capacity | Job per year | 4944
29.9.2 | 25 Ltr/hr capacity | Job per year | 8333
29.9.3 | 50 Ltr/hr capacity | Job per year | 14832
29.9.4 | 500 Ltr/hr capacity | Job per year | 55550
29.10. | All in all comprehensive maintenance of Domestic water purifier including replacement of components, consumables, cleaning, servicing etc. complete in all respect to meet efficient performance of the equipment. | Job per year | 2478
29.11 | All in all comprehensive maintenance of single/double Skin package type evaporative air cooling plant during defect liability period including air washer section, humidification section, fan section with motor, starter panel , water pump, ducting, grills etc. as per OEM's guidelines and standard terms & conditions of PWD to meet efficient performance of the equipment. | per 100 CFM per Year | 93
29.12 | All in all comprehensive maintenance of central air cooling plant including motor with blower, air washer section with nozzles, drift eliminators, starter panel, water pump, ducting, grills etc. complete in all respect as per OEM's guidelines and standard terms & conditions of PWD to meet efficient performance of the equipment. | per 100 CFM per Year | 123
29.13 | All in all comprehensive maintenance of forced ventilation system including fan section with motor, starter panel, CO senser, ducting grills etc. as per OEM's guidelines and standard terms & conditions of PWD to meet maximum efficiency of the machine. | per 100 CFM per Year | 73
29.14 | All in all comprehensive maintenance of central air conditioning system including air cooled chiller and its control , AHU's , FCU's , Hot water generator , LT/APFC panels , Control Panel , Pipe line and pumps , valves , ducting , grills / diffusers , consumables etc. complete in all respect as per OEM's guidelines and standard terms & conditions of PWD to meet out the maximum efficiency of the machine. | Per Ton per Year | 2378
29.15 | All in all comprehensive maintenance of central air conditioning system including water cooled chiller and its control , AHU's , FCU's , Hot water generator , cooling tower with associated accessories , LT/APFC panels , Control Panel , Pipe line and pumps , valves , ducting , grills /diffusers , consumables etc. complete in all respect as per OEM's guidelines and standard terms & conditions of PWD to meet out the maximum efficiency of the machine. | Per Ton per Year | 2811
29.16 | All in all comprehensive maintenance of Package type air conditioning system including indoor units , out door units ,ducting , grills , consumables , cabling , starting panel etc. complete in all respect as per OEM's guidelines and standard terms & conditions of PWD to meet out the maximum efficiency of the machine. | Per Ton per Year | 1878
29.17 | All in all comprehensive maintenance of Variable refrigerant volume (VRV) air conditioning system including indoor units , out door units , cordless control , refrigerant piping , control cables , remote control , drain piping , consumables , LT panel etc. complete in all respect as per OEM's guidelines and standard terms & conditions of PWD to meet out the maximum efficiency of the machine. | per outdoor HP per year | 2589
29.18 | All in all comprehensive maintenance of mono block / submersible motor pump set with starter panel etc. complete in all respect
29.18.1 | Mono block Motor pump set | Per HP per Year | 1300
29.18.2 | Sub mersible Motor pump set | Per HP per Year | 1728
NOTE:- Payment of lowering and delowering of pump shall be made extra subject to verification of Engineer Incharge.
29.18.3 | Mud pump Motor set | Per HP per Year | 3089
29.18.4 | Pressure boosting Motor pump set | Per HP per Year | 4944
28.19 | All in all comprehensive maintenance of fire detection control system, manual call point , response indicators , speakers/hooters . PA system , wiring/cabling etc complete in all respect as per OEM's recommendations / guidelines and standard terms & conditions of PWD guide lines to put the system healthy and functional .
28.19.1 | Addressable type FACP with repeater panel, all types of detectors & devices (total 125 Nos) , fault isolation module , | Per loop per Year | 14832
28.19.2 | Conventional type FACP with detectors & devices | Per Zone per yr. | 2778
29.20. | All in all comprehensive maintenance of fire protection system including jockey Pump , main motor pump , terrace pump , Diesel pump , water sprinkles pipe lines ,wet /dry risers , various type of valves , over head / under ground water tanks , First aid hose reels , Indoor / out door hydrants , air vessels , hose pipes , branch pipes , hose cabinets , control panel , all type of fire extinguishers , battery charger ,wiring/cabling etc. complete in all respect. and standard terms & conditions of PWD (including replacement of battery and refilling of fire extinguishers .)
29.20.1 | 1620 LPM, 56 Mtr Head main pump fire station | Job per year | 49384
29.20.2 | 1620 LPM, 70 Mtr Head main pump fire station | Job per year | 54284
29.20.3 | 2280 /2250 LPM, 70 Mtr Head main pump fire station | Job per year | 69104
29.20.4 | 2280 /2250 LPM, 88 Mtr Head main pump fire station | Job per year | 82658
29.20.5 | 2850 LPM, 70 Mtr Head main pump fire station | Job per year | 94991
29.20.6 | 2850 LPM, 88 Mtr Head main pump fire station | Job per year | 99935
29.20.7 | 4500 LPM, 70 Mtr Head main pump fire station | Job per year | 106101
29.20.8 | 4500 LPM, 88 Mtr Head main pump fire station | Job per year | 118433
29.21 | All in all annual maintenance and repair charges of various make refrigerator (Fridge) including charging of refrigerant, replacement of compressor, relay, thermostate,Timer, indicating lamp,etc complete in all respect of following capacity
29.21.1 | up to 210 litre capacity | Job per year | 1408
29.21.2 | above 210 & up to 400 litre capacity | Job per year | 1951
29.22 | All in all Comprehensive annual maintenance and repair contract for On line UPS of following Capacity ( Excluding Replacement of Batteries )
29.22.1 | 600 VA UPS | Job per year | 333
29.22.2 | 1 KVA UPS | Job per year | 2778
29.22.3 | 2 KVA UPS | Job per year | 3333
29.22.4 | 3 KVA UPS | Job per year | 4166
29.22.5 | 5/6 KVA UPS | Job per year | 8333
29.22.6 | 10 KVA UPS | Job per year | 13332
29.22.7 | 15 KVA UPS | Job per year | 16665
29.22.8 | 20 KVA UPS | Job per year | 22220
29.22.9 | 30 KVA UPS | Job per year | 33330